## Slide 1
AVESTA · EL MO3ALEM JUICE SHOP
Solar + battery: option by option
Option A, then B, then C: equations and results for each system, followed by one final comparison
Basis: August 2026 bill · commercial tariff (EgyptERA, April 2026) · no maintenance or interest included
Notes: Sources: EgyptERA commercial tariff from April 2026, https://www.egyptera.org/en/TarrifApril2026.aspx (checked 30 Sep 2026). JRC PVGIS 5.3, https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023, Cairo 30.0444N 31.2357E, south-facing 30 degrees, crystalline silicon, free-standing, 14% entered PV loss. Historical modeled output, local shading unmeasured. Home_Storage.pptx slide 15: battery 220 EUR/kWh at assumed 62 EGP/EUR = 13,640 EGP/kWh. Historical model assumptions treated as customer selling prices, not current quotes. Source deck slide 18 states 10-year warranty and 6,000 cycles at 80% DoD.
Method: E=2421/30=80.7 kWh/day (billing period assumed). D=N=40.35. U=C*0.8 before losses. eta=0.95 aggregate storage-path energy factor allocated once at output. Delivered battery=min(solar surplus*eta,U*eta,N). No grid charging, exports have zero value, no reserve held. Required whole-night nameplate=40.35/(.8*.95)=53.092105 kWh. Installed C=64 for the product comparison. PV size rounded up to 0.5 kWp. Inverter sizes preliminary.
Annual scenario: monthly PV daily mean=PVGIS E_m / calendar days, daily consumption held at80.7, non-leap year365days. Treat each month as repeated average days, no hourly dispatch or interday simulation. Baseline bill and newbill evaluated per month at full precision. Rounded displayed inputs may create small rounding differences. All savings exclude the equal annual3EGP stamp, which cancels in the comparison. No finance, maintenance, insurance, degradation, replacement, tariff escalation or added subscription margin.
PVGIS annual API total1818.36kWh vs summed rounded monthly1818.37kWh differs by0.01 due to rounding. Sizing uses requested unweighted mean of12 displayed daily yields4.9816667 rounded4.98. Annual financial calculation uses monthly E_m.
Calculated reference and monthly scenarios (unrounded):
[
{
"option": "A",
"C": 0,
"P": 8.5,
"inv": 10,
"price": 140800,
"reference": {
"G": 42.330000000000005,
"direct": 40.35,
"surplus": 1.980000000000004,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 36.00161290322581,
"direct": 36.00161290322581,
"surplus": 0,
"battery": 0,
"imports": 1385.6499999999999,
"base": 7094.794000000002,
"newbill": 3947.533,
"saving": 3147.261000000002
},
{
"month": "Feb",
"days": 28,
"G": 39.29732142857142,
"direct": 39.29732142857142,
"surplus": 0,
"battery": 0,
"imports": 1159.2750000000003,
"base": 6412.071999999999,
"newbill": 3309.1555000000008,
"saving": 3102.9164999999985
},
{
"month": "Mar",
"days": 31,
"G": 44.1616129032258,
"direct": 40.35,
"surplus": 3.8116129032258,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Apr",
"days": 30,
"G": 45.577,
"direct": 40.35,
"surplus": 5.226999999999997,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "May",
"days": 31,
"G": 44.61677419354839,
"direct": 40.35,
"surplus": 4.266774193548386,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Jun",
"days": 30,
"G": 44.94233333333334,
"direct": 40.35,
"surplus": 4.592333333333336,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Jul",
"days": 31,
"G": 45.148709677419355,
"direct": 40.35,
"surplus": 4.798709677419353,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Aug",
"days": 31,
"G": 45.73548387096774,
"direct": 40.35,
"surplus": 5.3854838709677395,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Sep",
"days": 30,
"G": 45.61666666666666,
"direct": 40.35,
"surplus": 5.266666666666659,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Oct",
"days": 31,
"G": 42.37112903225807,
"direct": 40.35,
"surplus": 2.0211290322580666,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Nov",
"days": 30,
"G": 38.80816666666667,
"direct": 38.80816666666667,
"surplus": 0,
"battery": 0,
"imports": 1256.7549999999999,
"base": 6867.22,
"newbill": 3584.0490999999997,
"saving": 3283.1709000000005
},
{
"month": "Dec",
"days": 31,
"G": 35.75483870967742,
"direct": 35.75483870967742,
"surplus": 0,
"battery": 0,
"imports": 1393.3,
"base": 7094.794000000002,
"newbill": 3969.1059999999998,
"saving": 3125.688000000002
}
],
"annualSaving": 40536.85140000001,
"averageSaving": 3378.0709500000007,
"payback": 3.4733827403279767,
"annualImports": 15080.73
},
{
"option": "B",
"C": 16,
"P": 11,
"inv": 12,
"price": 394240,
"reference": {
"G": 54.78,
"direct": 40.35,
"surplus": 14.43,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 46.59032258064517,
"direct": 40.35,
"surplus": 6.24032258064517,
"battery": 5.928306451612912,
"imports": 1067.0724999999998,
"base": 7094.794000000002,
"newbill": 3049.1444499999993,
"saving": 4045.6495500000024
},
{
"month": "Feb",
"days": 28,
"G": 50.85535714285714,
"direct": 40.35,
"surplus": 10.505357142857136,
"battery": 9.980089285714278,
"imports": 850.3575000000003,
"base": 6412.071999999999,
"newbill": 2320.490275000001,
"saving": 4091.581724999998
},
{
"month": "Mar",
"days": 31,
"G": 57.15032258064516,
"direct": 40.35,
"surplus": 16.800322580645158,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Apr",
"days": 30,
"G": 58.982,
"direct": 40.35,
"surplus": 18.631999999999998,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "May",
"days": 31,
"G": 57.73935483870968,
"direct": 40.35,
"surplus": 17.38935483870968,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Jun",
"days": 30,
"G": 58.16066666666667,
"direct": 40.35,
"surplus": 17.81066666666667,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Jul",
"days": 31,
"G": 58.42774193548387,
"direct": 40.35,
"surplus": 18.07774193548387,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Aug",
"days": 31,
"G": 59.18709677419355,
"direct": 40.35,
"surplus": 18.837096774193547,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Sep",
"days": 30,
"G": 59.03333333333333,
"direct": 40.35,
"surplus": 18.68333333333333,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Oct",
"days": 31,
"G": 54.833225806451615,
"direct": 40.35,
"surplus": 14.483225806451614,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Nov",
"days": 30,
"G": 50.22233333333334,
"direct": 40.35,
"surplus": 9.872333333333337,
"battery": 9.37871666666667,
"imports": 929.1385,
"base": 6867.22,
"newbill": 2538.7136450000003,
"saving": 4328.5063549999995
},
{
"month": "Dec",
"days": 31,
"G": 46.27096774193549,
"direct": 40.35,
"surplus": 5.920967741935492,
"battery": 5.624919354838717,
"imports": 1076.4774999999997,
"base": 7094.794000000002,
"newbill": 3075.666549999999,
"saving": 4019.1274500000027
}
],
"annualSaving": 53709.35158,
"averageSaving": 4475.779298333334,
"payback": 7.340248735134701,
"annualImports": 10829.596
},
{
"option": "C",
"C": 64,
"P": 17,
"inv": 20,
"price": 1154560,
"reference": {
"G": 84.66000000000001,
"direct": 40.35,
"surplus": 44.31000000000001,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 72.00322580645162,
"direct": 40.35,
"surplus": 31.653225806451623,
"battery": 30.07056451612904,
"imports": 318.66249999999985,
"base": 7094.794000000002,
"newbill": 870.8288749999997,
"saving": 6223.965125000002
},
{
"month": "Feb",
"days": 28,
"G": 78.59464285714284,
"direct": 40.35,
"surplus": 38.24464285714284,
"battery": 36.3324107142857,
"imports": 112.49250000000043,
"base": 6412.071999999999,
"newbill": 261.35857500000094,
"saving": 6150.713424999998
},
{
"month": "Mar",
"days": 31,
"G": 88.3232258064516,
"direct": 40.35,
"surplus": 47.9732258064516,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Apr",
"days": 30,
"G": 91.154,
"direct": 40.35,
"surplus": 50.803999999999995,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "May",
"days": 31,
"G": 89.23354838709677,
"direct": 40.35,
"surplus": 48.88354838709677,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Jun",
"days": 30,
"G": 89.88466666666667,
"direct": 40.35,
"surplus": 49.53466666666667,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Jul",
"days": 31,
"G": 90.29741935483871,
"direct": 40.35,
"surplus": 49.94741935483871,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Aug",
"days": 31,
"G": 91.47096774193548,
"direct": 40.35,
"surplus": 51.12096774193548,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Sep",
"days": 30,
"G": 91.23333333333332,
"direct": 40.35,
"surplus": 50.88333333333332,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Oct",
"days": 31,
"G": 84.74225806451614,
"direct": 40.35,
"surplus": 44.392258064516135,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Nov",
"days": 30,
"G": 77.61633333333334,
"direct": 40.35,
"surplus": 37.26633333333334,
"battery": 35.40301666666667,
"imports": 148.40949999999987,
"base": 6867.22,
"newbill": 340.01680499999975,
"saving": 6527.203195
},
{
"month": "Dec",
"days": 31,
"G": 71.50967741935484,
"direct": 40.35,
"surplus": 31.159677419354843,
"battery": 29.6016935483871,
"imports": 333.19749999999993,
"base": 7094.794000000002,
"newbill": 909.6373249999998,
"saving": 6185.156675000002
}
],
"annualSaving": 81090.66842000002,
"averageSaving": 6757.555701666668,
"payback": 14.237889790476089,
"annualImports": 912.7620000000002
}
]

## Slide 2
THE SHOP TODAY
2,421 kWh a month, refrigeration around the clock
2,421
kWh per month 312,070 − 309,649
80.7
kWh per day E = 2,421 ÷ 30
6,867
EGP per month at the official tariff
50%
assumed night share 50% day / 50% night
Receipt: 8,279 EGP. Tariff model: 6,867.22 EGP. The 1,411.78 EGP difference needs the detailed invoice.
Daily use assumes a 30-day billing period. The 50/50 split is an unmeasured scenario.
Monthly kWh | EGP / kWh | Service fee (EGP)
1–100 | 1.62, all units | 5
101–250 | 2.16, all units | 15
251–600 | 2.64, all units | 20
601–1,000 | 2.64 / 2.74* | 25
Above 1,000 | 2.79, all units | 40
Zero use | — | 9
Commercial tariff and monthly bill
Bill = energy + service + 0.03 × kWh
2,421 × 2.79 = 6,754.59
+ 40 + 72.63 = 6,867.22 EGP
*601–1,000: first 600 at 2.64, rest at 2.74.
Consumption stamp: 0.03 EGP/kWh.
Source: EgyptERA, commercial tariff from April 2026. Annual 3 EGP stamp excluded equally from both cases.
Notes: Sources: EgyptERA commercial tariff from April 2026, https://www.egyptera.org/en/TarrifApril2026.aspx (checked 30 Sep 2026). JRC PVGIS 5.3, https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023, Cairo 30.0444N 31.2357E, south-facing 30 degrees, crystalline silicon, free-standing, 14% entered PV loss. Historical modeled output, local shading unmeasured. Home_Storage.pptx slide 15: battery 220 EUR/kWh at assumed 62 EGP/EUR = 13,640 EGP/kWh. Historical model assumptions treated as customer selling prices, not current quotes. Source deck slide 18 states 10-year warranty and 6,000 cycles at 80% DoD.
Method: E=2421/30=80.7 kWh/day (billing period assumed). D=N=40.35. U=C*0.8 before losses. eta=0.95 aggregate storage-path energy factor allocated once at output. Delivered battery=min(solar surplus*eta,U*eta,N). No grid charging, exports have zero value, no reserve held. Required whole-night nameplate=40.35/(.8*.95)=53.092105 kWh. Installed C=64 for the product comparison. PV size rounded up to 0.5 kWp. Inverter sizes preliminary.
Annual scenario: monthly PV daily mean=PVGIS E_m / calendar days, daily consumption held at80.7, non-leap year365days. Treat each month as repeated average days, no hourly dispatch or interday simulation. Baseline bill and newbill evaluated per month at full precision. Rounded displayed inputs may create small rounding differences. All savings exclude the equal annual3EGP stamp, which cancels in the comparison. No finance, maintenance, insurance, degradation, replacement, tariff escalation or added subscription margin.
PVGIS annual API total1818.36kWh vs summed rounded monthly1818.37kWh differs by0.01 due to rounding. Sizing uses requested unweighted mean of12 displayed daily yields4.9816667 rounded4.98. Annual financial calculation uses monthly E_m.
Calculated reference and monthly scenarios (unrounded):
[
{
"option": "A",
"C": 0,
"P": 8.5,
"inv": 10,
"price": 140800,
"reference": {
"G": 42.330000000000005,
"direct": 40.35,
"surplus": 1.980000000000004,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 36.00161290322581,
"direct": 36.00161290322581,
"surplus": 0,
"battery": 0,
"imports": 1385.6499999999999,
"base": 7094.794000000002,
"newbill": 3947.533,
"saving": 3147.261000000002
},
{
"month": "Feb",
"days": 28,
"G": 39.29732142857142,
"direct": 39.29732142857142,
"surplus": 0,
"battery": 0,
"imports": 1159.2750000000003,
"base": 6412.071999999999,
"newbill": 3309.1555000000008,
"saving": 3102.9164999999985
},
{
"month": "Mar",
"days": 31,
"G": 44.1616129032258,
"direct": 40.35,
"surplus": 3.8116129032258,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Apr",
"days": 30,
"G": 45.577,
"direct": 40.35,
"surplus": 5.226999999999997,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "May",
"days": 31,
"G": 44.61677419354839,
"direct": 40.35,
"surplus": 4.266774193548386,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Jun",
"days": 30,
"G": 44.94233333333334,
"direct": 40.35,
"surplus": 4.592333333333336,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Jul",
"days": 31,
"G": 45.148709677419355,
"direct": 40.35,
"surplus": 4.798709677419353,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Aug",
"days": 31,
"G": 45.73548387096774,
"direct": 40.35,
"surplus": 5.3854838709677395,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Sep",
"days": 30,
"G": 45.61666666666666,
"direct": 40.35,
"surplus": 5.266666666666659,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Oct",
"days": 31,
"G": 42.37112903225807,
"direct": 40.35,
"surplus": 2.0211290322580666,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Nov",
"days": 30,
"G": 38.80816666666667,
"direct": 38.80816666666667,
"surplus": 0,
"battery": 0,
"imports": 1256.7549999999999,
"base": 6867.22,
"newbill": 3584.0490999999997,
"saving": 3283.1709000000005
},
{
"month": "Dec",
"days": 31,
"G": 35.75483870967742,
"direct": 35.75483870967742,
"surplus": 0,
"battery": 0,
"imports": 1393.3,
"base": 7094.794000000002,
"newbill": 3969.1059999999998,
"saving": 3125.688000000002
}
],
"annualSaving": 40536.85140000001,
"averageSaving": 3378.0709500000007,
"payback": 3.4733827403279767,
"annualImports": 15080.73
},
{
"option": "B",
"C": 16,
"P": 11,
"inv": 12,
"price": 394240,
"reference": {
"G": 54.78,
"direct": 40.35,
"surplus": 14.43,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 46.59032258064517,
"direct": 40.35,
"surplus": 6.24032258064517,
"battery": 5.928306451612912,
"imports": 1067.0724999999998,
"base": 7094.794000000002,
"newbill": 3049.1444499999993,
"saving": 4045.6495500000024
},
{
"month": "Feb",
"days": 28,
"G": 50.85535714285714,
"direct": 40.35,
"surplus": 10.505357142857136,
"battery": 9.980089285714278,
"imports": 850.3575000000003,
"base": 6412.071999999999,
"newbill": 2320.490275000001,
"saving": 4091.581724999998
},
{
"month": "Mar",
"days": 31,
"G": 57.15032258064516,
"direct": 40.35,
"surplus": 16.800322580645158,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Apr",
"days": 30,
"G": 58.982,
"direct": 40.35,
"surplus": 18.631999999999998,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "May",
"days": 31,
"G": 57.73935483870968,
"direct": 40.35,
"surplus": 17.38935483870968,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Jun",
"days": 30,
"G": 58.16066666666667,
"direct": 40.35,
"surplus": 17.81066666666667,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Jul",
"days": 31,
"G": 58.42774193548387,
"direct": 40.35,
"surplus": 18.07774193548387,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Aug",
"days": 31,
"G": 59.18709677419355,
"direct": 40.35,
"surplus": 18.837096774193547,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Sep",
"days": 30,
"G": 59.03333333333333,
"direct": 40.35,
"surplus": 18.68333333333333,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Oct",
"days": 31,
"G": 54.833225806451615,
"direct": 40.35,
"surplus": 14.483225806451614,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Nov",
"days": 30,
"G": 50.22233333333334,
"direct": 40.35,
"surplus": 9.872333333333337,
"battery": 9.37871666666667,
"imports": 929.1385,
"base": 6867.22,
"newbill": 2538.7136450000003,
"saving": 4328.5063549999995
},
{
"month": "Dec",
"days": 31,
"G": 46.27096774193549,
"direct": 40.35,
"surplus": 5.920967741935492,
"battery": 5.624919354838717,
"imports": 1076.4774999999997,
"base": 7094.794000000002,
"newbill": 3075.666549999999,
"saving": 4019.1274500000027
}
],
"annualSaving": 53709.35158,
"averageSaving": 4475.779298333334,
"payback": 7.340248735134701,
"annualImports": 10829.596
},
{
"option": "C",
"C": 64,
"P": 17,
"inv": 20,
"price": 1154560,
"reference": {
"G": 84.66000000000001,
"direct": 40.35,
"surplus": 44.31000000000001,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 72.00322580645162,
"direct": 40.35,
"surplus": 31.653225806451623,
"battery": 30.07056451612904,
"imports": 318.66249999999985,
"base": 7094.794000000002,
"newbill": 870.8288749999997,
"saving": 6223.965125000002
},
{
"month": "Feb",
"days": 28,
"G": 78.59464285714284,
"direct": 40.35,
"surplus": 38.24464285714284,
"battery": 36.3324107142857,
"imports": 112.49250000000043,
"base": 6412.071999999999,
"newbill": 261.35857500000094,
"saving": 6150.713424999998
},
{
"month": "Mar",
"days": 31,
"G": 88.3232258064516,
"direct": 40.35,
"surplus": 47.9732258064516,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Apr",
"days": 30,
"G": 91.154,
"direct": 40.35,
"surplus": 50.803999999999995,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "May",
"days": 31,
"G": 89.23354838709677,
"direct": 40.35,
"surplus": 48.88354838709677,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Jun",
"days": 30,
"G": 89.88466666666667,
"direct": 40.35,
"surplus": 49.53466666666667,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Jul",
"days": 31,
"G": 90.29741935483871,
"direct": 40.35,
"surplus": 49.94741935483871,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Aug",
"days": 31,
"G": 91.47096774193548,
"direct": 40.35,
"surplus": 51.12096774193548,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Sep",
"days": 30,
"G": 91.23333333333332,
"direct": 40.35,
"surplus": 50.88333333333332,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Oct",
"days": 31,
"G": 84.74225806451614,
"direct": 40.35,
"surplus": 44.392258064516135,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Nov",
"days": 30,
"G": 77.61633333333334,
"direct": 40.35,
"surplus": 37.26633333333334,
"battery": 35.40301666666667,
"imports": 148.40949999999987,
"base": 6867.22,
"newbill": 340.01680499999975,
"saving": 6527.203195
},
{
"month": "Dec",
"days": 31,
"G": 71.50967741935484,
"direct": 40.35,
"surplus": 31.159677419354843,
"battery": 29.6016935483871,
"imports": 333.19749999999993,
"base": 7094.794000000002,
"newbill": 909.6373249999998,
"saving": 6185.156675000002
}
],
"annualSaving": 81090.66842000002,
"averageSaving": 6757.555701666668,
"payback": 14.237889790476089,
"annualImports": 912.7620000000002
}
]

## Slide 3
REFERENCE · PVGIS CAIRO
Monthly solar electricity production
Reference system: 1 kWp. A 550 W panel is shown as an illustrative panel size.
Month | Daily / 1 kWp (kWh/day) | Monthly / 1 kWp (kWh/month) | Daily / 550 W panel (kWh/day)
January | 4.24 | 131.30 | 2.33
February | 4.62 | 129.45 | 2.54
March | 5.20 | 161.06 | 2.86
April | 5.36 | 160.86 | 2.95
May | 5.25 | 162.72 | 2.89
June | 5.29 | 158.62 | 2.91
July | 5.31 | 164.66 | 2.92
August | 5.38 | 166.80 | 2.96
September | 5.37 | 161.00 | 2.95
October | 4.98 | 154.53 | 2.74
November | 4.57 | 136.97 | 2.51
December | 4.21 | 130.40 | 2.32
JRC PVGIS 5.3 · SARAH3 / ERA5 (2005–2023) · Cairo 30.0444 N, 31.2357 E · retrieved 30 Sep 2026
South-facing, 30° tilt, crystalline silicon, free-standing, 14% entered system loss; local roof shading not surveyed.
Notes: Sources: EgyptERA commercial tariff from April 2026, https://www.egyptera.org/en/TarrifApril2026.aspx (checked 30 Sep 2026). JRC PVGIS 5.3, https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023, Cairo 30.0444N 31.2357E, south-facing 30 degrees, crystalline silicon, free-standing, 14% entered PV loss. Historical modeled output, local shading unmeasured. Home_Storage.pptx slide 15: battery 220 EUR/kWh at assumed 62 EGP/EUR = 13,640 EGP/kWh. Historical model assumptions treated as customer selling prices, not current quotes. Source deck slide 18 states 10-year warranty and 6,000 cycles at 80% DoD.
Method: E=2421/30=80.7 kWh/day (billing period assumed). D=N=40.35. U=C*0.8 before losses. eta=0.95 aggregate storage-path energy factor allocated once at output. Delivered battery=min(solar surplus*eta,U*eta,N). No grid charging, exports have zero value, no reserve held. Required whole-night nameplate=40.35/(.8*.95)=53.092105 kWh. Installed C=64 for the product comparison. PV size rounded up to 0.5 kWp. Inverter sizes preliminary.
Annual scenario: monthly PV daily mean=PVGIS E_m / calendar days, daily consumption held at80.7, non-leap year365days. Treat each month as repeated average days, no hourly dispatch or interday simulation. Baseline bill and newbill evaluated per month at full precision. Rounded displayed inputs may create small rounding differences. All savings exclude the equal annual3EGP stamp, which cancels in the comparison. No finance, maintenance, insurance, degradation, replacement, tariff escalation or added subscription margin.
PVGIS annual API total1818.36kWh vs summed rounded monthly1818.37kWh differs by0.01 due to rounding. Sizing uses requested unweighted mean of12 displayed daily yields4.9816667 rounded4.98. Annual financial calculation uses monthly E_m.
Calculated reference and monthly scenarios (unrounded):
[
{
"option": "A",
"C": 0,
"P": 8.5,
"inv": 10,
"price": 140800,
"reference": {
"G": 42.330000000000005,
"direct": 40.35,
"surplus": 1.980000000000004,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 36.00161290322581,
"direct": 36.00161290322581,
"surplus": 0,
"battery": 0,
"imports": 1385.6499999999999,
"base": 7094.794000000002,
"newbill": 3947.533,
"saving": 3147.261000000002
},
{
"month": "Feb",
"days": 28,
"G": 39.29732142857142,
"direct": 39.29732142857142,
"surplus": 0,
"battery": 0,
"imports": 1159.2750000000003,
"base": 6412.071999999999,
"newbill": 3309.1555000000008,
"saving": 3102.9164999999985
},
{
"month": "Mar",
"days": 31,
"G": 44.1616129032258,
"direct": 40.35,
"surplus": 3.8116129032258,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Apr",
"days": 30,
"G": 45.577,
"direct": 40.35,
"surplus": 5.226999999999997,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "May",
"days": 31,
"G": 44.61677419354839,
"direct": 40.35,
"surplus": 4.266774193548386,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Jun",
"days": 30,
"G": 44.94233333333334,
"direct": 40.35,
"surplus": 4.592333333333336,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Jul",
"days": 31,
"G": 45.148709677419355,
"direct": 40.35,
"surplus": 4.798709677419353,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Aug",
"days": 31,
"G": 45.73548387096774,
"direct": 40.35,
"surplus": 5.3854838709677395,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Sep",
"days": 30,
"G": 45.61666666666666,
"direct": 40.35,
"surplus": 5.266666666666659,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Oct",
"days": 31,
"G": 42.37112903225807,
"direct": 40.35,
"surplus": 2.0211290322580666,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Nov",
"days": 30,
"G": 38.80816666666667,
"direct": 38.80816666666667,
"surplus": 0,
"battery": 0,
"imports": 1256.7549999999999,
"base": 6867.22,
"newbill": 3584.0490999999997,
"saving": 3283.1709000000005
},
{
"month": "Dec",
"days": 31,
"G": 35.75483870967742,
"direct": 35.75483870967742,
"surplus": 0,
"battery": 0,
"imports": 1393.3,
"base": 7094.794000000002,
"newbill": 3969.1059999999998,
"saving": 3125.688000000002
}
],
"annualSaving": 40536.85140000001,
"averageSaving": 3378.0709500000007,
"payback": 3.4733827403279767,
"annualImports": 15080.73
},
{
"option": "B",
"C": 16,
"P": 11,
"inv": 12,
"price": 394240,
"reference": {
"G": 54.78,
"direct": 40.35,
"surplus": 14.43,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 46.59032258064517,
"direct": 40.35,
"surplus": 6.24032258064517,
"battery": 5.928306451612912,
"imports": 1067.0724999999998,
"base": 7094.794000000002,
"newbill": 3049.1444499999993,
"saving": 4045.6495500000024
},
{
"month": "Feb",
"days": 28,
"G": 50.85535714285714,
"direct": 40.35,
"surplus": 10.505357142857136,
"battery": 9.980089285714278,
"imports": 850.3575000000003,
"base": 6412.071999999999,
"newbill": 2320.490275000001,
"saving": 4091.581724999998
},
{
"month": "Mar",
"days": 31,
"G": 57.15032258064516,
"direct": 40.35,
"surplus": 16.800322580645158,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Apr",
"days": 30,
"G": 58.982,
"direct": 40.35,
"surplus": 18.631999999999998,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "May",
"days": 31,
"G": 57.73935483870968,
"direct": 40.35,
"surplus": 17.38935483870968,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Jun",
"days": 30,
"G": 58.16066666666667,
"direct": 40.35,
"surplus": 17.81066666666667,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Jul",
"days": 31,
"G": 58.42774193548387,
"direct": 40.35,
"surplus": 18.07774193548387,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Aug",
"days": 31,
"G": 59.18709677419355,
"direct": 40.35,
"surplus": 18.837096774193547,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Sep",
"days": 30,
"G": 59.03333333333333,
"direct": 40.35,
"surplus": 18.68333333333333,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Oct",
"days": 31,
"G": 54.833225806451615,
"direct": 40.35,
"surplus": 14.483225806451614,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Nov",
"days": 30,
"G": 50.22233333333334,
"direct": 40.35,
"surplus": 9.872333333333337,
"battery": 9.37871666666667,
"imports": 929.1385,
"base": 6867.22,
"newbill": 2538.7136450000003,
"saving": 4328.5063549999995
},
{
"month": "Dec",
"days": 31,
"G": 46.27096774193549,
"direct": 40.35,
"surplus": 5.920967741935492,
"battery": 5.624919354838717,
"imports": 1076.4774999999997,
"base": 7094.794000000002,
"newbill": 3075.666549999999,
"saving": 4019.1274500000027
}
],
"annualSaving": 53709.35158,
"averageSaving": 4475.779298333334,
"payback": 7.340248735134701,
"annualImports": 10829.596
},
{
"option": "C",
"C": 64,
"P": 17,
"inv": 20,
"price": 1154560,
"reference": {
"G": 84.66000000000001,
"direct": 40.35,
"surplus": 44.31000000000001,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 72.00322580645162,
"direct": 40.35,
"surplus": 31.653225806451623,
"battery": 30.07056451612904,
"imports": 318.66249999999985,
"base": 7094.794000000002,
"newbill": 870.8288749999997,
"saving": 6223.965125000002
},
{
"month": "Feb",
"days": 28,
"G": 78.59464285714284,
"direct": 40.35,
"surplus": 38.24464285714284,
"battery": 36.3324107142857,
"imports": 112.49250000000043,
"base": 6412.071999999999,
"newbill": 261.35857500000094,
"saving": 6150.713424999998
},
{
"month": "Mar",
"days": 31,
"G": 88.3232258064516,
"direct": 40.35,
"surplus": 47.9732258064516,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Apr",
"days": 30,
"G": 91.154,
"direct": 40.35,
"surplus": 50.803999999999995,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "May",
"days": 31,
"G": 89.23354838709677,
"direct": 40.35,
"surplus": 48.88354838709677,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Jun",
"days": 30,
"G": 89.88466666666667,
"direct": 40.35,
"surplus": 49.53466666666667,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Jul",
"days": 31,
"G": 90.29741935483871,
"direct": 40.35,
"surplus": 49.94741935483871,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Aug",
"days": 31,
"G": 91.47096774193548,
"direct": 40.35,
"surplus": 51.12096774193548,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Sep",
"days": 30,
"G": 91.23333333333332,
"direct": 40.35,
"surplus": 50.88333333333332,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Oct",
"days": 31,
"G": 84.74225806451614,
"direct": 40.35,
"surplus": 44.392258064516135,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Nov",
"days": 30,
"G": 77.61633333333334,
"direct": 40.35,
"surplus": 37.26633333333334,
"battery": 35.40301666666667,
"imports": 148.40949999999987,
"base": 6867.22,
"newbill": 340.01680499999975,
"saving": 6527.203195
},
{
"month": "Dec",
"days": 31,
"G": 71.50967741935484,
"direct": 40.35,
"surplus": 31.159677419354843,
"battery": 29.6016935483871,
"imports": 333.19749999999993,
"base": 7094.794000000002,
"newbill": 909.6373249999998,
"saving": 6185.156675000002
}
],
"annualSaving": 81090.66842000002,
"averageSaving": 6757.555701666668,
"payback": 14.237889790476089,
"annualImports": 912.7620000000002
}
]

## Slide 4
REFERENCE · AVERAGES AND SETTINGS
How the Cairo average is calculated
Average of the 12 daily monthly values
(4.24 + 4.62 + 5.20 + 5.36 + 5.25 + 5.29 + 5.31 + 5.38 + 5.37 + 4.98 + 4.57 + 4.21) ÷ 12
= 4.9817 ≈ 4.98 kWh/kWp/day
Average monthly output = sum of monthly outputs ÷ 12 = 151.53 kWh/kWp/month
Annual output = 1,818.36 kWh/kWp/year; annual daily average = 1818.36 ÷ 365 ≈ 4.9818
Example: 550 W = 0.55 kWp → average daily output ≈ 0.55 × 4.98 = 2.74 kWh/day
The 1,750 kWh/year estimate is replaced by this sourced reference calculation.
PVGIS electricity output already includes modeled PV losses; battery losses are additional.
These are historical climate averages. Actual output varies by month, weather, shading and cleaning.
Source: European Commission JRC PVGIS 5.3 · inputs and full calculation URL are in speaker notes.
Notes: Sources: EgyptERA commercial tariff from April 2026, https://www.egyptera.org/en/TarrifApril2026.aspx (checked 30 Sep 2026). JRC PVGIS 5.3, https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023, Cairo 30.0444N 31.2357E, south-facing 30 degrees, crystalline silicon, free-standing, 14% entered PV loss. Historical modeled output, local shading unmeasured. Home_Storage.pptx slide 15: battery 220 EUR/kWh at assumed 62 EGP/EUR = 13,640 EGP/kWh. Historical model assumptions treated as customer selling prices, not current quotes. Source deck slide 18 states 10-year warranty and 6,000 cycles at 80% DoD.
Method: E=2421/30=80.7 kWh/day (billing period assumed). D=N=40.35. U=C*0.8 before losses. eta=0.95 aggregate storage-path energy factor allocated once at output. Delivered battery=min(solar surplus*eta,U*eta,N). No grid charging, exports have zero value, no reserve held. Required whole-night nameplate=40.35/(.8*.95)=53.092105 kWh. Installed C=64 for the product comparison. PV size rounded up to 0.5 kWp. Inverter sizes preliminary.
Annual scenario: monthly PV daily mean=PVGIS E_m / calendar days, daily consumption held at80.7, non-leap year365days. Treat each month as repeated average days, no hourly dispatch or interday simulation. Baseline bill and newbill evaluated per month at full precision. Rounded displayed inputs may create small rounding differences. All savings exclude the equal annual3EGP stamp, which cancels in the comparison. No finance, maintenance, insurance, degradation, replacement, tariff escalation or added subscription margin.
PVGIS annual API total1818.36kWh vs summed rounded monthly1818.37kWh differs by0.01 due to rounding. Sizing uses requested unweighted mean of12 displayed daily yields4.9816667 rounded4.98. Annual financial calculation uses monthly E_m.
Calculated reference and monthly scenarios (unrounded):
[
{
"option": "A",
"C": 0,
"P": 8.5,
"inv": 10,
"price": 140800,
"reference": {
"G": 42.330000000000005,
"direct": 40.35,
"surplus": 1.980000000000004,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 36.00161290322581,
"direct": 36.00161290322581,
"surplus": 0,
"battery": 0,
"imports": 1385.6499999999999,
"base": 7094.794000000002,
"newbill": 3947.533,
"saving": 3147.261000000002
},
{
"month": "Feb",
"days": 28,
"G": 39.29732142857142,
"direct": 39.29732142857142,
"surplus": 0,
"battery": 0,
"imports": 1159.2750000000003,
"base": 6412.071999999999,
"newbill": 3309.1555000000008,
"saving": 3102.9164999999985
},
{
"month": "Mar",
"days": 31,
"G": 44.1616129032258,
"direct": 40.35,
"surplus": 3.8116129032258,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Apr",
"days": 30,
"G": 45.577,
"direct": 40.35,
"surplus": 5.226999999999997,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "May",
"days": 31,
"G": 44.61677419354839,
"direct": 40.35,
"surplus": 4.266774193548386,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Jun",
"days": 30,
"G": 44.94233333333334,
"direct": 40.35,
"surplus": 4.592333333333336,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Jul",
"days": 31,
"G": 45.148709677419355,
"direct": 40.35,
"surplus": 4.798709677419353,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Aug",
"days": 31,
"G": 45.73548387096774,
"direct": 40.35,
"surplus": 5.3854838709677395,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Sep",
"days": 30,
"G": 45.61666666666666,
"direct": 40.35,
"surplus": 5.266666666666659,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Oct",
"days": 31,
"G": 42.37112903225807,
"direct": 40.35,
"surplus": 2.0211290322580666,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Nov",
"days": 30,
"G": 38.80816666666667,
"direct": 38.80816666666667,
"surplus": 0,
"battery": 0,
"imports": 1256.7549999999999,
"base": 6867.22,
"newbill": 3584.0490999999997,
"saving": 3283.1709000000005
},
{
"month": "Dec",
"days": 31,
"G": 35.75483870967742,
"direct": 35.75483870967742,
"surplus": 0,
"battery": 0,
"imports": 1393.3,
"base": 7094.794000000002,
"newbill": 3969.1059999999998,
"saving": 3125.688000000002
}
],
"annualSaving": 40536.85140000001,
"averageSaving": 3378.0709500000007,
"payback": 3.4733827403279767,
"annualImports": 15080.73
},
{
"option": "B",
"C": 16,
"P": 11,
"inv": 12,
"price": 394240,
"reference": {
"G": 54.78,
"direct": 40.35,
"surplus": 14.43,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 46.59032258064517,
"direct": 40.35,
"surplus": 6.24032258064517,
"battery": 5.928306451612912,
"imports": 1067.0724999999998,
"base": 7094.794000000002,
"newbill": 3049.1444499999993,
"saving": 4045.6495500000024
},
{
"month": "Feb",
"days": 28,
"G": 50.85535714285714,
"direct": 40.35,
"surplus": 10.505357142857136,
"battery": 9.980089285714278,
"imports": 850.3575000000003,
"base": 6412.071999999999,
"newbill": 2320.490275000001,
"saving": 4091.581724999998
},
{
"month": "Mar",
"days": 31,
"G": 57.15032258064516,
"direct": 40.35,
"surplus": 16.800322580645158,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Apr",
"days": 30,
"G": 58.982,
"direct": 40.35,
"surplus": 18.631999999999998,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "May",
"days": 31,
"G": 57.73935483870968,
"direct": 40.35,
"surplus": 17.38935483870968,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Jun",
"days": 30,
"G": 58.16066666666667,
"direct": 40.35,
"surplus": 17.81066666666667,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Jul",
"days": 31,
"G": 58.42774193548387,
"direct": 40.35,
"surplus": 18.07774193548387,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Aug",
"days": 31,
"G": 59.18709677419355,
"direct": 40.35,
"surplus": 18.837096774193547,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Sep",
"days": 30,
"G": 59.03333333333333,
"direct": 40.35,
"surplus": 18.68333333333333,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Oct",
"days": 31,
"G": 54.833225806451615,
"direct": 40.35,
"surplus": 14.483225806451614,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Nov",
"days": 30,
"G": 50.22233333333334,
"direct": 40.35,
"surplus": 9.872333333333337,
"battery": 9.37871666666667,
"imports": 929.1385,
"base": 6867.22,
"newbill": 2538.7136450000003,
"saving": 4328.5063549999995
},
{
"month": "Dec",
"days": 31,
"G": 46.27096774193549,
"direct": 40.35,
"surplus": 5.920967741935492,
"battery": 5.624919354838717,
"imports": 1076.4774999999997,
"base": 7094.794000000002,
"newbill": 3075.666549999999,
"saving": 4019.1274500000027
}
],
"annualSaving": 53709.35158,
"averageSaving": 4475.779298333334,
"payback": 7.340248735134701,
"annualImports": 10829.596
},
{
"option": "C",
"C": 64,
"P": 17,
"inv": 20,
"price": 1154560,
"reference": {
"G": 84.66000000000001,
"direct": 40.35,
"surplus": 44.31000000000001,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 72.00322580645162,
"direct": 40.35,
"surplus": 31.653225806451623,
"battery": 30.07056451612904,
"imports": 318.66249999999985,
"base": 7094.794000000002,
"newbill": 870.8288749999997,
"saving": 6223.965125000002
},
{
"month": "Feb",
"days": 28,
"G": 78.59464285714284,
"direct": 40.35,
"surplus": 38.24464285714284,
"battery": 36.3324107142857,
"imports": 112.49250000000043,
"base": 6412.071999999999,
"newbill": 261.35857500000094,
"saving": 6150.713424999998
},
{
"month": "Mar",
"days": 31,
"G": 88.3232258064516,
"direct": 40.35,
"surplus": 47.9732258064516,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Apr",
"days": 30,
"G": 91.154,
"direct": 40.35,
"surplus": 50.803999999999995,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "May",
"days": 31,
"G": 89.23354838709677,
"direct": 40.35,
"surplus": 48.88354838709677,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Jun",
"days": 30,
"G": 89.88466666666667,
"direct": 40.35,
"surplus": 49.53466666666667,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Jul",
"days": 31,
"G": 90.29741935483871,
"direct": 40.35,
"surplus": 49.94741935483871,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Aug",
"days": 31,
"G": 91.47096774193548,
"direct": 40.35,
"surplus": 51.12096774193548,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Sep",
"days": 30,
"G": 91.23333333333332,
"direct": 40.35,
"surplus": 50.88333333333332,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Oct",
"days": 31,
"G": 84.74225806451614,
"direct": 40.35,
"surplus": 44.392258064516135,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Nov",
"days": 30,
"G": 77.61633333333334,
"direct": 40.35,
"surplus": 37.26633333333334,
"battery": 35.40301666666667,
"imports": 148.40949999999987,
"base": 6867.22,
"newbill": 340.01680499999975,
"saving": 6527.203195
},
{
"month": "Dec",
"days": 31,
"G": 71.50967741935484,
"direct": 40.35,
"surplus": 31.159677419354843,
"battery": 29.6016935483871,
"imports": 333.19749999999993,
"base": 7094.794000000002,
"newbill": 909.6373249999998,
"saving": 6185.156675000002
}
],
"annualSaving": 81090.66842000002,
"averageSaving": 6757.555701666668,
"payback": 14.237889790476089,
"annualImports": 912.7620000000002
}
]

## Slide 5
REFERENCE
Assumptions and open points
Item | Value | Source / status
Monthly use | 2,421 kWh | Meter difference. 30-day period assumed
Modeled bill | 6,867.22 EGP | Receipt 8,279 EGP: reconcile the difference
Day / night share | 50% / 50% | Scenario, not a measured hourly profile
PV output | 4.98 kWh/kWp/day | Sizing mean. Monthly PVGIS for finances (3–4)
DoD / efficiency | 80% / 95% | 95% lumped once on delivered storage energy
Price inputs | 13,640 / 8,000 / 6,000 | EGP per battery kWh / PV kWp / inverter kW
Cost exclusions | O&M / finance / degradation | Also no replacement, insurance or escalation
Annual load | 80.7 kWh/day all year | Constant-load scenario. Seasonality unknown
Needed: detailed invoice, actual billing dates, 12 months of consumption, hourly loads, roof survey and motor starting current.
Energy matching assumes all daily solar up to daytime demand can be used directly. Hourly mismatch can lower savings.
Notes: Sources: EgyptERA commercial tariff from April 2026, https://www.egyptera.org/en/TarrifApril2026.aspx (checked 30 Sep 2026). JRC PVGIS 5.3, https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023, Cairo 30.0444N 31.2357E, south-facing 30 degrees, crystalline silicon, free-standing, 14% entered PV loss. Historical modeled output, local shading unmeasured. Home_Storage.pptx slide 15: battery 220 EUR/kWh at assumed 62 EGP/EUR = 13,640 EGP/kWh. Historical model assumptions treated as customer selling prices, not current quotes. Source deck slide 18 states 10-year warranty and 6,000 cycles at 80% DoD.
Method: E=2421/30=80.7 kWh/day (billing period assumed). D=N=40.35. U=C*0.8 before losses. eta=0.95 aggregate storage-path energy factor allocated once at output. Delivered battery=min(solar surplus*eta,U*eta,N). No grid charging, exports have zero value, no reserve held. Required whole-night nameplate=40.35/(.8*.95)=53.092105 kWh. Installed C=64 for the product comparison. PV size rounded up to 0.5 kWp. Inverter sizes preliminary.
Annual scenario: monthly PV daily mean=PVGIS E_m / calendar days, daily consumption held at80.7, non-leap year365days. Treat each month as repeated average days, no hourly dispatch or interday simulation. Baseline bill and newbill evaluated per month at full precision. Rounded displayed inputs may create small rounding differences. All savings exclude the equal annual3EGP stamp, which cancels in the comparison. No finance, maintenance, insurance, degradation, replacement, tariff escalation or added subscription margin.
PVGIS annual API total1818.36kWh vs summed rounded monthly1818.37kWh differs by0.01 due to rounding. Sizing uses requested unweighted mean of12 displayed daily yields4.9816667 rounded4.98. Annual financial calculation uses monthly E_m.
Calculated reference and monthly scenarios (unrounded):
[
{
"option": "A",
"C": 0,
"P": 8.5,
"inv": 10,
"price": 140800,
"reference": {
"G": 42.330000000000005,
"direct": 40.35,
"surplus": 1.980000000000004,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 36.00161290322581,
"direct": 36.00161290322581,
"surplus": 0,
"battery": 0,
"imports": 1385.6499999999999,
"base": 7094.794000000002,
"newbill": 3947.533,
"saving": 3147.261000000002
},
{
"month": "Feb",
"days": 28,
"G": 39.29732142857142,
"direct": 39.29732142857142,
"surplus": 0,
"battery": 0,
"imports": 1159.2750000000003,
"base": 6412.071999999999,
"newbill": 3309.1555000000008,
"saving": 3102.9164999999985
},
{
"month": "Mar",
"days": 31,
"G": 44.1616129032258,
"direct": 40.35,
"surplus": 3.8116129032258,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Apr",
"days": 30,
"G": 45.577,
"direct": 40.35,
"surplus": 5.226999999999997,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "May",
"days": 31,
"G": 44.61677419354839,
"direct": 40.35,
"surplus": 4.266774193548386,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Jun",
"days": 30,
"G": 44.94233333333334,
"direct": 40.35,
"surplus": 4.592333333333336,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Jul",
"days": 31,
"G": 45.148709677419355,
"direct": 40.35,
"surplus": 4.798709677419353,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Aug",
"days": 31,
"G": 45.73548387096774,
"direct": 40.35,
"surplus": 5.3854838709677395,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Sep",
"days": 30,
"G": 45.61666666666666,
"direct": 40.35,
"surplus": 5.266666666666659,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Oct",
"days": 31,
"G": 42.37112903225807,
"direct": 40.35,
"surplus": 2.0211290322580666,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Nov",
"days": 30,
"G": 38.80816666666667,
"direct": 38.80816666666667,
"surplus": 0,
"battery": 0,
"imports": 1256.7549999999999,
"base": 6867.22,
"newbill": 3584.0490999999997,
"saving": 3283.1709000000005
},
{
"month": "Dec",
"days": 31,
"G": 35.75483870967742,
"direct": 35.75483870967742,
"surplus": 0,
"battery": 0,
"imports": 1393.3,
"base": 7094.794000000002,
"newbill": 3969.1059999999998,
"saving": 3125.688000000002
}
],
"annualSaving": 40536.85140000001,
"averageSaving": 3378.0709500000007,
"payback": 3.4733827403279767,
"annualImports": 15080.73
},
{
"option": "B",
"C": 16,
"P": 11,
"inv": 12,
"price": 394240,
"reference": {
"G": 54.78,
"direct": 40.35,
"surplus": 14.43,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 46.59032258064517,
"direct": 40.35,
"surplus": 6.24032258064517,
"battery": 5.928306451612912,
"imports": 1067.0724999999998,
"base": 7094.794000000002,
"newbill": 3049.1444499999993,
"saving": 4045.6495500000024
},
{
"month": "Feb",
"days": 28,
"G": 50.85535714285714,
"direct": 40.35,
"surplus": 10.505357142857136,
"battery": 9.980089285714278,
"imports": 850.3575000000003,
"base": 6412.071999999999,
"newbill": 2320.490275000001,
"saving": 4091.581724999998
},
{
"month": "Mar",
"days": 31,
"G": 57.15032258064516,
"direct": 40.35,
"surplus": 16.800322580645158,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Apr",
"days": 30,
"G": 58.982,
"direct": 40.35,
"surplus": 18.631999999999998,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "May",
"days": 31,
"G": 57.73935483870968,
"direct": 40.35,
"surplus": 17.38935483870968,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Jun",
"days": 30,
"G": 58.16066666666667,
"direct": 40.35,
"surplus": 17.81066666666667,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Jul",
"days": 31,
"G": 58.42774193548387,
"direct": 40.35,
"surplus": 18.07774193548387,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Aug",
"days": 31,
"G": 59.18709677419355,
"direct": 40.35,
"surplus": 18.837096774193547,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Sep",
"days": 30,
"G": 59.03333333333333,
"direct": 40.35,
"surplus": 18.68333333333333,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Oct",
"days": 31,
"G": 54.833225806451615,
"direct": 40.35,
"surplus": 14.483225806451614,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Nov",
"days": 30,
"G": 50.22233333333334,
"direct": 40.35,
"surplus": 9.872333333333337,
"battery": 9.37871666666667,
"imports": 929.1385,
"base": 6867.22,
"newbill": 2538.7136450000003,
"saving": 4328.5063549999995
},
{
"month": "Dec",
"days": 31,
"G": 46.27096774193549,
"direct": 40.35,
"surplus": 5.920967741935492,
"battery": 5.624919354838717,
"imports": 1076.4774999999997,
"base": 7094.794000000002,
"newbill": 3075.666549999999,
"saving": 4019.1274500000027
}
],
"annualSaving": 53709.35158,
"averageSaving": 4475.779298333334,
"payback": 7.340248735134701,
"annualImports": 10829.596
},
{
"option": "C",
"C": 64,
"P": 17,
"inv": 20,
"price": 1154560,
"reference": {
"G": 84.66000000000001,
"direct": 40.35,
"surplus": 44.31000000000001,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 72.00322580645162,
"direct": 40.35,
"surplus": 31.653225806451623,
"battery": 30.07056451612904,
"imports": 318.66249999999985,
"base": 7094.794000000002,
"newbill": 870.8288749999997,
"saving": 6223.965125000002
},
{
"month": "Feb",
"days": 28,
"G": 78.59464285714284,
"direct": 40.35,
"surplus": 38.24464285714284,
"battery": 36.3324107142857,
"imports": 112.49250000000043,
"base": 6412.071999999999,
"newbill": 261.35857500000094,
"saving": 6150.713424999998
},
{
"month": "Mar",
"days": 31,
"G": 88.3232258064516,
"direct": 40.35,
"surplus": 47.9732258064516,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Apr",
"days": 30,
"G": 91.154,
"direct": 40.35,
"surplus": 50.803999999999995,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "May",
"days": 31,
"G": 89.23354838709677,
"direct": 40.35,
"surplus": 48.88354838709677,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Jun",
"days": 30,
"G": 89.88466666666667,
"direct": 40.35,
"surplus": 49.53466666666667,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Jul",
"days": 31,
"G": 90.29741935483871,
"direct": 40.35,
"surplus": 49.94741935483871,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Aug",
"days": 31,
"G": 91.47096774193548,
"direct": 40.35,
"surplus": 51.12096774193548,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Sep",
"days": 30,
"G": 91.23333333333332,
"direct": 40.35,
"surplus": 50.88333333333332,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Oct",
"days": 31,
"G": 84.74225806451614,
"direct": 40.35,
"surplus": 44.392258064516135,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Nov",
"days": 30,
"G": 77.61633333333334,
"direct": 40.35,
"surplus": 37.26633333333334,
"battery": 35.40301666666667,
"imports": 148.40949999999987,
"base": 6867.22,
"newbill": 340.01680499999975,
"saving": 6527.203195
},
{
"month": "Dec",
"days": 31,
"G": 71.50967741935484,
"direct": 40.35,
"surplus": 31.159677419354843,
"battery": 29.6016935483871,
"imports": 333.19749999999993,
"base": 7094.794000000002,
"newbill": 909.6373249999998,
"saving": 6185.156675000002
}
],
"annualSaving": 81090.66842000002,
"averageSaving": 6757.555701666668,
"payback": 14.237889790476089,
"annualImports": 912.7620000000002
}
]

## Slide 6
OPTION A · SOLAR ONLY
1. Daily demand and system sizing
Daily demand and its split
E = 2,421 / 30 = 80.70 kWh/day; D = N = E × 50% = 40.35
Battery capacity and energy delivered
C = 0 kWh; U = C × 80% = 0; U × 95% = 0 kWh
PV capacity, rounded up to the next 0.5 kWp
P = (D + min(N, U × η) / η) / Y
= (40.35 + 0.00 / 0.95) / 4.98 = 8.102 → 8.5 kWp
Provisional inverter and roof allowance
Selected inverter I = 10 kW (standard size ≥ P); roof ≈ 8.5 × 6 = 51 m²
Solar covers daytime energy in the average-day model. No battery energy is available for night or stored backup.
50/50 is an unmeasured assumption. Confirm motor surge and usable roof area.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
{
"option": "A",
"C": 0,
"P": 8.5,
"inv": 10,
"price": 140800,
"reference": {
"G": 42.330000000000005,
"direct": 40.35,
"surplus": 1.980000000000004,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 36.00161290322581,
"direct": 36.00161290322581,
"surplus": 0,
"battery": 0,
"imports": 1385.6499999999999,
"base": 7094.794000000002,
"newbill": 3947.533,
"saving": 3147.261000000002
},
{
"month": "Feb",
"days": 28,
"G": 39.29732142857142,
"direct": 39.29732142857142,
"surplus": 0,
"battery": 0,
"imports": 1159.2750000000003,
"base": 6412.071999999999,
"newbill": 3309.1555000000008,
"saving": 3102.9164999999985
},
{
"month": "Mar",
"days": 31,
"G": 44.1616129032258,
"direct": 40.35,
"surplus": 3.8116129032258,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Apr",
"days": 30,
"G": 45.577,
"direct": 40.35,
"surplus": 5.226999999999997,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "May",
"days": 31,
"G": 44.61677419354839,
"direct": 40.35,
"surplus": 4.266774193548386,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Jun",
"days": 30,
"G": 44.94233333333334,
"direct": 40.35,
"surplus": 4.592333333333336,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Jul",
"days": 31,
"G": 45.148709677419355,
"direct": 40.35,
"surplus": 4.798709677419353,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Aug",
"days": 31,
"G": 45.73548387096774,
"direct": 40.35,
"surplus": 5.3854838709677395,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Sep",
"days": 30,
"G": 45.61666666666666,
"direct": 40.35,
"surplus": 5.266666666666659,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Oct",
"days": 31,
"G": 42.37112903225807,
"direct": 40.35,
"surplus": 2.0211290322580666,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Nov",
"days": 30,
"G": 38.80816666666667,
"direct": 38.80816666666667,
"surplus": 0,
"battery": 0,
"imports": 1256.7549999999999,
"base": 6867.22,
"newbill": 3584.0490999999997,
"saving": 3283.1709000000005
},
{
"month": "Dec",
"days": 31,
"G": 35.75483870967742,
"direct": 35.75483870967742,
"surplus": 0,
"battery": 0,
"imports": 1393.3,
"base": 7094.794000000002,
"newbill": 3969.1059999999998,
"saving": 3125.688000000002
}
],
"annualSaving": 40536.85140000001,
"averageSaving": 3378.0709500000007,
"payback": 3.4733827403279767,
"annualImports": 15080.73
}

## Slide 7
OPTION A · SOLAR ONLY
2. System price
Unit-price assumptions
PV = 8,000 EGP/kWp; inverter = 6,000 EGP/kW
Battery = 220 EUR/kWh × 62 EGP/EUR = 13,640 EGP/kWh
PV and inverter subtotal
8.5 × 8,000 + 10 × 6,000 = 128,000 EGP
Installation / BOS and battery cost
Installation = 128,000 × 10% = 12,800 EGP
Battery = 0 × 13,640 = 0 EGP
Total customer price
Price = (8.5 × 8,000 + 10 × 6,000) × 1.10 + 0 × 13,640
= 140,800 EGP
The 10% installation/BOS applies to PV and inverter only. Battery price comes from Home_Storage, slide 15.
Customer selling-price assumptions, including historical exchange rate 62 EGP/EUR. These are not current quotes.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
{
"option": "A",
"C": 0,
"P": 8.5,
"inv": 10,
"price": 140800,
"reference": {
"G": 42.330000000000005,
"direct": 40.35,
"surplus": 1.980000000000004,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 36.00161290322581,
"direct": 36.00161290322581,
"surplus": 0,
"battery": 0,
"imports": 1385.6499999999999,
"base": 7094.794000000002,
"newbill": 3947.533,
"saving": 3147.261000000002
},
{
"month": "Feb",
"days": 28,
"G": 39.29732142857142,
"direct": 39.29732142857142,
"surplus": 0,
"battery": 0,
"imports": 1159.2750000000003,
"base": 6412.071999999999,
"newbill": 3309.1555000000008,
"saving": 3102.9164999999985
},
{
"month": "Mar",
"days": 31,
"G": 44.1616129032258,
"direct": 40.35,
"surplus": 3.8116129032258,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Apr",
"days": 30,
"G": 45.577,
"direct": 40.35,
"surplus": 5.226999999999997,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "May",
"days": 31,
"G": 44.61677419354839,
"direct": 40.35,
"surplus": 4.266774193548386,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Jun",
"days": 30,
"G": 44.94233333333334,
"direct": 40.35,
"surplus": 4.592333333333336,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Jul",
"days": 31,
"G": 45.148709677419355,
"direct": 40.35,
"surplus": 4.798709677419353,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Aug",
"days": 31,
"G": 45.73548387096774,
"direct": 40.35,
"surplus": 5.3854838709677395,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Sep",
"days": 30,
"G": 45.61666666666666,
"direct": 40.35,
"surplus": 5.266666666666659,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Oct",
"days": 31,
"G": 42.37112903225807,
"direct": 40.35,
"surplus": 2.0211290322580666,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Nov",
"days": 30,
"G": 38.80816666666667,
"direct": 38.80816666666667,
"surplus": 0,
"battery": 0,
"imports": 1256.7549999999999,
"base": 6867.22,
"newbill": 3584.0490999999997,
"saving": 3283.1709000000005
},
{
"month": "Dec",
"days": 31,
"G": 35.75483870967742,
"direct": 35.75483870967742,
"surplus": 0,
"battery": 0,
"imports": 1393.3,
"base": 7094.794000000002,
"newbill": 3969.1059999999998,
"saving": 3125.688000000002
}
],
"annualSaving": 40536.85140000001,
"averageSaving": 3378.0709500000007,
"payback": 3.4733827403279767,
"annualImports": 15080.73
}

## Slide 8
OPTION A · SOLAR ONLY
3. Energy balance and the monthly bill
Solar generation and direct use
G = P × Y = 8.5 × 4.98 = 42.33 kWh/day
Direct = min(G, D) = 40.35; surplus = G − Direct = 1.98
Battery energy delivered to the loads
B = min(surplus × η, U × η, N)
= min(1.88, 0.00, 40.35) = 0.00 kWh/day
Grid imports in the 30-day reference month
M_grid = (E − Direct − B) × 30
= (80.70 − 40.35 − 0.00) × 30 = 1,210.50 kWh
New bill and monthly saving
Bill = 1,210.50 × 2.79 + 40 + 1,210.50 × 0.03 = 3,453.61 EGP
Saving = 6,867.22 − 3,453.61 = 3,413.61 EGP
This is a 30-day example at Y = 4.98. Solar charges the battery. Surplus export earns zero revenue.
Storage losses are applied once. The annual calculation on the next slide accounts for monthly solar variation.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
{
"option": "A",
"C": 0,
"P": 8.5,
"inv": 10,
"price": 140800,
"reference": {
"G": 42.330000000000005,
"direct": 40.35,
"surplus": 1.980000000000004,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 36.00161290322581,
"direct": 36.00161290322581,
"surplus": 0,
"battery": 0,
"imports": 1385.6499999999999,
"base": 7094.794000000002,
"newbill": 3947.533,
"saving": 3147.261000000002
},
{
"month": "Feb",
"days": 28,
"G": 39.29732142857142,
"direct": 39.29732142857142,
"surplus": 0,
"battery": 0,
"imports": 1159.2750000000003,
"base": 6412.071999999999,
"newbill": 3309.1555000000008,
"saving": 3102.9164999999985
},
{
"month": "Mar",
"days": 31,
"G": 44.1616129032258,
"direct": 40.35,
"surplus": 3.8116129032258,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Apr",
"days": 30,
"G": 45.577,
"direct": 40.35,
"surplus": 5.226999999999997,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "May",
"days": 31,
"G": 44.61677419354839,
"direct": 40.35,
"surplus": 4.266774193548386,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Jun",
"days": 30,
"G": 44.94233333333334,
"direct": 40.35,
"surplus": 4.592333333333336,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Jul",
"days": 31,
"G": 45.148709677419355,
"direct": 40.35,
"surplus": 4.798709677419353,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Aug",
"days": 31,
"G": 45.73548387096774,
"direct": 40.35,
"surplus": 5.3854838709677395,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Sep",
"days": 30,
"G": 45.61666666666666,
"direct": 40.35,
"surplus": 5.266666666666659,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Oct",
"days": 31,
"G": 42.37112903225807,
"direct": 40.35,
"surplus": 2.0211290322580666,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Nov",
"days": 30,
"G": 38.80816666666667,
"direct": 38.80816666666667,
"surplus": 0,
"battery": 0,
"imports": 1256.7549999999999,
"base": 6867.22,
"newbill": 3584.0490999999997,
"saving": 3283.1709000000005
},
{
"month": "Dec",
"days": 31,
"G": 35.75483870967742,
"direct": 35.75483870967742,
"surplus": 0,
"battery": 0,
"imports": 1393.3,
"base": 7094.794000000002,
"newbill": 3969.1059999999998,
"saving": 3125.688000000002
}
],
"annualSaving": 40536.85140000001,
"averageSaving": 3378.0709500000007,
"payback": 3.4733827403279767,
"annualImports": 15080.73
}

## Slide 9
OPTION A · SOLAR ONLY
4. Twelve monthly results and annual saving
Each month: daily PV = P × PVGIS monthly kWh/kWp ÷ days. Grid = (E − Direct − B) × days.
Month | Days | PV kWh | Grid kWh | Baseline EGP | New bill EGP | Saving EGP
Jan | 31 | 1,116.05 | 1,385.65 | 7,094.79 | 3,947.53 | 3,147.26
Feb | 28 | 1,100.32 | 1,159.28 | 6,412.07 | 3,309.16 | 3,102.92
Mar | 31 | 1,369.01 | 1,250.85 | 7,094.79 | 3,567.40 | 3,527.40
Apr | 30 | 1,367.31 | 1,210.50 | 6,867.22 | 3,453.61 | 3,413.61
May | 31 | 1,383.12 | 1,250.85 | 7,094.79 | 3,567.40 | 3,527.40
Jun | 30 | 1,348.27 | 1,210.50 | 6,867.22 | 3,453.61 | 3,413.61
Jul | 31 | 1,399.61 | 1,250.85 | 7,094.79 | 3,567.40 | 3,527.40
Aug | 31 | 1,417.80 | 1,250.85 | 7,094.79 | 3,567.40 | 3,527.40
Sep | 30 | 1,368.50 | 1,210.50 | 6,867.22 | 3,453.61 | 3,413.61
Oct | 31 | 1,313.51 | 1,250.85 | 7,094.79 | 3,567.40 | 3,527.40
Nov | 30 | 1,164.25 | 1,256.75 | 6,867.22 | 3,584.05 | 3,283.17
Dec | 31 | 1,108.40 | 1,393.30 | 7,094.79 | 3,969.11 | 3,125.69
Year | 365 | 15,456.15 | 15,080.73 | 83,544.51 | 43,007.66 | 40,536.85
Annual saving = sum of monthly savings = 40,536.85 EGP. Average/month = annual / 12 = 3,378.07 EGP.
Constant demand: 80.7 kWh/day, 50/50 split. Monthly average days, no hourly simulation. Displayed figures are rounded.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
{
"option": "A",
"C": 0,
"P": 8.5,
"inv": 10,
"price": 140800,
"reference": {
"G": 42.330000000000005,
"direct": 40.35,
"surplus": 1.980000000000004,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 36.00161290322581,
"direct": 36.00161290322581,
"surplus": 0,
"battery": 0,
"imports": 1385.6499999999999,
"base": 7094.794000000002,
"newbill": 3947.533,
"saving": 3147.261000000002
},
{
"month": "Feb",
"days": 28,
"G": 39.29732142857142,
"direct": 39.29732142857142,
"surplus": 0,
"battery": 0,
"imports": 1159.2750000000003,
"base": 6412.071999999999,
"newbill": 3309.1555000000008,
"saving": 3102.9164999999985
},
{
"month": "Mar",
"days": 31,
"G": 44.1616129032258,
"direct": 40.35,
"surplus": 3.8116129032258,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Apr",
"days": 30,
"G": 45.577,
"direct": 40.35,
"surplus": 5.226999999999997,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "May",
"days": 31,
"G": 44.61677419354839,
"direct": 40.35,
"surplus": 4.266774193548386,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Jun",
"days": 30,
"G": 44.94233333333334,
"direct": 40.35,
"surplus": 4.592333333333336,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Jul",
"days": 31,
"G": 45.148709677419355,
"direct": 40.35,
"surplus": 4.798709677419353,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Aug",
"days": 31,
"G": 45.73548387096774,
"direct": 40.35,
"surplus": 5.3854838709677395,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Sep",
"days": 30,
"G": 45.61666666666666,
"direct": 40.35,
"surplus": 5.266666666666659,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Oct",
"days": 31,
"G": 42.37112903225807,
"direct": 40.35,
"surplus": 2.0211290322580666,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Nov",
"days": 30,
"G": 38.80816666666667,
"direct": 38.80816666666667,
"surplus": 0,
"battery": 0,
"imports": 1256.7549999999999,
"base": 6867.22,
"newbill": 3584.0490999999997,
"saving": 3283.1709000000005
},
{
"month": "Dec",
"days": 31,
"G": 35.75483870967742,
"direct": 35.75483870967742,
"surplus": 0,
"battery": 0,
"imports": 1393.3,
"base": 7094.794000000002,
"newbill": 3969.1059999999998,
"saving": 3125.688000000002
}
],
"annualSaving": 40536.85140000001,
"averageSaving": 3378.0709500000007,
"payback": 3.4733827403279767,
"annualImports": 15080.73
}

## Slide 10
OPTION A · SOLAR ONLY
5. Purchase payback and subscription
Simple payback = price / annual saving
= 140,800 / 40,536.85 = 3.47 years
Monthly fee = price / (term in years × 12)
Average net benefit/month = annual saving / 12 − monthly fee
Term | Fee calculation | Fee EGP/month | Avg. net EGP/month
5 years | 140,800 / (5 × 12) | 2,346.67 | 1,031.40
8 years | 140,800 / (8 × 12) | 1,466.67 | 1,911.40
10 years | 140,800 / (10 × 12) | 1,173.33 | 2,204.74
Break-even term = price / annual saving = 3.47 years, where the average net benefit is zero.
Illustrative recovery of selling price. No extra subscription margin, maintenance, insurance, financing or replacement.
No degradation or tariff increases. Monthly benefits vary. Simple payback is not a discounted return calculation.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
{
"option": "A",
"C": 0,
"P": 8.5,
"inv": 10,
"price": 140800,
"reference": {
"G": 42.330000000000005,
"direct": 40.35,
"surplus": 1.980000000000004,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 36.00161290322581,
"direct": 36.00161290322581,
"surplus": 0,
"battery": 0,
"imports": 1385.6499999999999,
"base": 7094.794000000002,
"newbill": 3947.533,
"saving": 3147.261000000002
},
{
"month": "Feb",
"days": 28,
"G": 39.29732142857142,
"direct": 39.29732142857142,
"surplus": 0,
"battery": 0,
"imports": 1159.2750000000003,
"base": 6412.071999999999,
"newbill": 3309.1555000000008,
"saving": 3102.9164999999985
},
{
"month": "Mar",
"days": 31,
"G": 44.1616129032258,
"direct": 40.35,
"surplus": 3.8116129032258,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Apr",
"days": 30,
"G": 45.577,
"direct": 40.35,
"surplus": 5.226999999999997,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "May",
"days": 31,
"G": 44.61677419354839,
"direct": 40.35,
"surplus": 4.266774193548386,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Jun",
"days": 30,
"G": 44.94233333333334,
"direct": 40.35,
"surplus": 4.592333333333336,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Jul",
"days": 31,
"G": 45.148709677419355,
"direct": 40.35,
"surplus": 4.798709677419353,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Aug",
"days": 31,
"G": 45.73548387096774,
"direct": 40.35,
"surplus": 5.3854838709677395,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Sep",
"days": 30,
"G": 45.61666666666666,
"direct": 40.35,
"surplus": 5.266666666666659,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Oct",
"days": 31,
"G": 42.37112903225807,
"direct": 40.35,
"surplus": 2.0211290322580666,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Nov",
"days": 30,
"G": 38.80816666666667,
"direct": 38.80816666666667,
"surplus": 0,
"battery": 0,
"imports": 1256.7549999999999,
"base": 6867.22,
"newbill": 3584.0490999999997,
"saving": 3283.1709000000005
},
{
"month": "Dec",
"days": 31,
"G": 35.75483870967742,
"direct": 35.75483870967742,
"surplus": 0,
"battery": 0,
"imports": 1393.3,
"base": 7094.794000000002,
"newbill": 3969.1059999999998,
"saving": 3125.688000000002
}
],
"annualSaving": 40536.85140000001,
"averageSaving": 3378.0709500000007,
"payback": 3.4733827403279767,
"annualImports": 15080.73
}

## Slide 11
OPTION B · SOLAR + ONE LV_16
1. Daily demand and system sizing
Daily demand and its split
E = 2,421 / 30 = 80.70 kWh/day; D = N = E × 50% = 40.35
Battery capacity and energy delivered
C = 16 kWh; U = C × 80% = 12.80; U × 95% = 12.16 kWh
PV capacity, rounded up to the next 0.5 kWp
P = (D + min(N, U × η) / η) / Y
= (40.35 + 12.16 / 0.95) / 4.98 = 10.673 → 11.0 kWp
Provisional inverter and roof allowance
Selected inverter I = 12 kW (standard size ≥ P); roof ≈ 11.0 × 6 = 66 m²
Partial-night storage. Backup estimate from full charge: 12.16 / (42.4 / 24) = 6.88 h for refrigeration only.
Night use reduces reserve. Confirm motor surge and an inverter that supports backup operation.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
{
"option": "B",
"C": 16,
"P": 11,
"inv": 12,
"price": 394240,
"reference": {
"G": 54.78,
"direct": 40.35,
"surplus": 14.43,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 46.59032258064517,
"direct": 40.35,
"surplus": 6.24032258064517,
"battery": 5.928306451612912,
"imports": 1067.0724999999998,
"base": 7094.794000000002,
"newbill": 3049.1444499999993,
"saving": 4045.6495500000024
},
{
"month": "Feb",
"days": 28,
"G": 50.85535714285714,
"direct": 40.35,
"surplus": 10.505357142857136,
"battery": 9.980089285714278,
"imports": 850.3575000000003,
"base": 6412.071999999999,
"newbill": 2320.490275000001,
"saving": 4091.581724999998
},
{
"month": "Mar",
"days": 31,
"G": 57.15032258064516,
"direct": 40.35,
"surplus": 16.800322580645158,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Apr",
"days": 30,
"G": 58.982,
"direct": 40.35,
"surplus": 18.631999999999998,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "May",
"days": 31,
"G": 57.73935483870968,
"direct": 40.35,
"surplus": 17.38935483870968,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Jun",
"days": 30,
"G": 58.16066666666667,
"direct": 40.35,
"surplus": 17.81066666666667,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Jul",
"days": 31,
"G": 58.42774193548387,
"direct": 40.35,
"surplus": 18.07774193548387,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Aug",
"days": 31,
"G": 59.18709677419355,
"direct": 40.35,
"surplus": 18.837096774193547,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Sep",
"days": 30,
"G": 59.03333333333333,
"direct": 40.35,
"surplus": 18.68333333333333,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Oct",
"days": 31,
"G": 54.833225806451615,
"direct": 40.35,
"surplus": 14.483225806451614,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Nov",
"days": 30,
"G": 50.22233333333334,
"direct": 40.35,
"surplus": 9.872333333333337,
"battery": 9.37871666666667,
"imports": 929.1385,
"base": 6867.22,
"newbill": 2538.7136450000003,
"saving": 4328.5063549999995
},
{
"month": "Dec",
"days": 31,
"G": 46.27096774193549,
"direct": 40.35,
"surplus": 5.920967741935492,
"battery": 5.624919354838717,
"imports": 1076.4774999999997,
"base": 7094.794000000002,
"newbill": 3075.666549999999,
"saving": 4019.1274500000027
}
],
"annualSaving": 53709.35158,
"averageSaving": 4475.779298333334,
"payback": 7.340248735134701,
"annualImports": 10829.596
}

## Slide 12
OPTION B · SOLAR + ONE LV_16
2. System price
Unit-price assumptions
PV = 8,000 EGP/kWp; inverter = 6,000 EGP/kW
Battery = 220 EUR/kWh × 62 EGP/EUR = 13,640 EGP/kWh
PV and inverter subtotal
11.0 × 8,000 + 12 × 6,000 = 160,000 EGP
Installation / BOS and battery cost
Installation = 160,000 × 10% = 16,000 EGP
Battery = 16 × 13,640 = 218,240 EGP
Total customer price
Price = (11.0 × 8,000 + 12 × 6,000) × 1.10 + 16 × 13,640
= 394,240 EGP
The 10% installation/BOS applies to PV and inverter only. Battery price comes from Home_Storage, slide 15.
Customer selling-price assumptions, including historical exchange rate 62 EGP/EUR. These are not current quotes.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
{
"option": "B",
"C": 16,
"P": 11,
"inv": 12,
"price": 394240,
"reference": {
"G": 54.78,
"direct": 40.35,
"surplus": 14.43,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 46.59032258064517,
"direct": 40.35,
"surplus": 6.24032258064517,
"battery": 5.928306451612912,
"imports": 1067.0724999999998,
"base": 7094.794000000002,
"newbill": 3049.1444499999993,
"saving": 4045.6495500000024
},
{
"month": "Feb",
"days": 28,
"G": 50.85535714285714,
"direct": 40.35,
"surplus": 10.505357142857136,
"battery": 9.980089285714278,
"imports": 850.3575000000003,
"base": 6412.071999999999,
"newbill": 2320.490275000001,
"saving": 4091.581724999998
},
{
"month": "Mar",
"days": 31,
"G": 57.15032258064516,
"direct": 40.35,
"surplus": 16.800322580645158,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Apr",
"days": 30,
"G": 58.982,
"direct": 40.35,
"surplus": 18.631999999999998,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "May",
"days": 31,
"G": 57.73935483870968,
"direct": 40.35,
"surplus": 17.38935483870968,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Jun",
"days": 30,
"G": 58.16066666666667,
"direct": 40.35,
"surplus": 17.81066666666667,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Jul",
"days": 31,
"G": 58.42774193548387,
"direct": 40.35,
"surplus": 18.07774193548387,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Aug",
"days": 31,
"G": 59.18709677419355,
"direct": 40.35,
"surplus": 18.837096774193547,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Sep",
"days": 30,
"G": 59.03333333333333,
"direct": 40.35,
"surplus": 18.68333333333333,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Oct",
"days": 31,
"G": 54.833225806451615,
"direct": 40.35,
"surplus": 14.483225806451614,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Nov",
"days": 30,
"G": 50.22233333333334,
"direct": 40.35,
"surplus": 9.872333333333337,
"battery": 9.37871666666667,
"imports": 929.1385,
"base": 6867.22,
"newbill": 2538.7136450000003,
"saving": 4328.5063549999995
},
{
"month": "Dec",
"days": 31,
"G": 46.27096774193549,
"direct": 40.35,
"surplus": 5.920967741935492,
"battery": 5.624919354838717,
"imports": 1076.4774999999997,
"base": 7094.794000000002,
"newbill": 3075.666549999999,
"saving": 4019.1274500000027
}
],
"annualSaving": 53709.35158,
"averageSaving": 4475.779298333334,
"payback": 7.340248735134701,
"annualImports": 10829.596
}

## Slide 13
OPTION B · SOLAR + ONE LV_16
3. Energy balance and the monthly bill
Solar generation and direct use
G = P × Y = 11.0 × 4.98 = 54.78 kWh/day
Direct = min(G, D) = 40.35; surplus = G − Direct = 14.43
Battery energy delivered to the loads
B = min(surplus × η, U × η, N)
= min(13.71, 12.16, 40.35) = 12.16 kWh/day
Grid imports in the 30-day reference month
M_grid = (E − Direct − B) × 30
= (80.70 − 40.35 − 12.16) × 30 = 845.70 kWh
New bill and monthly saving
Bill = 600 × 2.64 + 245.70 × 2.74 + 25 + 845.70 × 0.03 = 2,307.59
Saving = 6,867.22 − 2,307.59 = 4,559.63 EGP
This is a 30-day example at Y = 4.98. Solar charges the battery. Surplus export earns zero revenue.
Storage losses are applied once. The annual calculation on the next slide accounts for monthly solar variation.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
{
"option": "B",
"C": 16,
"P": 11,
"inv": 12,
"price": 394240,
"reference": {
"G": 54.78,
"direct": 40.35,
"surplus": 14.43,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 46.59032258064517,
"direct": 40.35,
"surplus": 6.24032258064517,
"battery": 5.928306451612912,
"imports": 1067.0724999999998,
"base": 7094.794000000002,
"newbill": 3049.1444499999993,
"saving": 4045.6495500000024
},
{
"month": "Feb",
"days": 28,
"G": 50.85535714285714,
"direct": 40.35,
"surplus": 10.505357142857136,
"battery": 9.980089285714278,
"imports": 850.3575000000003,
"base": 6412.071999999999,
"newbill": 2320.490275000001,
"saving": 4091.581724999998
},
{
"month": "Mar",
"days": 31,
"G": 57.15032258064516,
"direct": 40.35,
"surplus": 16.800322580645158,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Apr",
"days": 30,
"G": 58.982,
"direct": 40.35,
"surplus": 18.631999999999998,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "May",
"days": 31,
"G": 57.73935483870968,
"direct": 40.35,
"surplus": 17.38935483870968,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Jun",
"days": 30,
"G": 58.16066666666667,
"direct": 40.35,
"surplus": 17.81066666666667,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Jul",
"days": 31,
"G": 58.42774193548387,
"direct": 40.35,
"surplus": 18.07774193548387,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Aug",
"days": 31,
"G": 59.18709677419355,
"direct": 40.35,
"surplus": 18.837096774193547,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Sep",
"days": 30,
"G": 59.03333333333333,
"direct": 40.35,
"surplus": 18.68333333333333,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Oct",
"days": 31,
"G": 54.833225806451615,
"direct": 40.35,
"surplus": 14.483225806451614,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Nov",
"days": 30,
"G": 50.22233333333334,
"direct": 40.35,
"surplus": 9.872333333333337,
"battery": 9.37871666666667,
"imports": 929.1385,
"base": 6867.22,
"newbill": 2538.7136450000003,
"saving": 4328.5063549999995
},
{
"month": "Dec",
"days": 31,
"G": 46.27096774193549,
"direct": 40.35,
"surplus": 5.920967741935492,
"battery": 5.624919354838717,
"imports": 1076.4774999999997,
"base": 7094.794000000002,
"newbill": 3075.666549999999,
"saving": 4019.1274500000027
}
],
"annualSaving": 53709.35158,
"averageSaving": 4475.779298333334,
"payback": 7.340248735134701,
"annualImports": 10829.596
}

## Slide 14
OPTION B · SOLAR + ONE LV_16
4. Twelve monthly results and annual saving
Each month: daily PV = P × PVGIS monthly kWh/kWp ÷ days. Grid = (E − Direct − B) × days.
Month | Days | PV kWh | Grid kWh | Baseline EGP | New bill EGP | Saving EGP
Jan | 31 | 1,444.30 | 1,067.07 | 7,094.79 | 3,049.14 | 4,045.65
Feb | 28 | 1,423.95 | 850.36 | 6,412.07 | 2,320.49 | 4,091.58
Mar | 31 | 1,771.66 | 873.89 | 7,094.79 | 2,385.68 | 4,709.12
Apr | 30 | 1,769.46 | 845.70 | 6,867.22 | 2,307.59 | 4,559.63
May | 31 | 1,789.92 | 873.89 | 7,094.79 | 2,385.68 | 4,709.12
Jun | 30 | 1,744.82 | 845.70 | 6,867.22 | 2,307.59 | 4,559.63
Jul | 31 | 1,811.26 | 873.89 | 7,094.79 | 2,385.68 | 4,709.12
Aug | 31 | 1,834.80 | 873.89 | 7,094.79 | 2,385.68 | 4,709.12
Sep | 30 | 1,771.00 | 845.70 | 6,867.22 | 2,307.59 | 4,559.63
Oct | 31 | 1,699.83 | 873.89 | 7,094.79 | 2,385.68 | 4,709.12
Nov | 30 | 1,506.67 | 929.14 | 6,867.22 | 2,538.71 | 4,328.51
Dec | 31 | 1,434.40 | 1,076.48 | 7,094.79 | 3,075.67 | 4,019.13
Year | 365 | 20,002.07 | 10,829.60 | 83,544.51 | 29,835.16 | 53,709.35
Annual saving = sum of monthly savings = 53,709.35 EGP. Average/month = annual / 12 = 4,475.78 EGP.
Constant demand: 80.7 kWh/day, 50/50 split. Monthly average days, no hourly simulation. Displayed figures are rounded.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
{
"option": "B",
"C": 16,
"P": 11,
"inv": 12,
"price": 394240,
"reference": {
"G": 54.78,
"direct": 40.35,
"surplus": 14.43,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 46.59032258064517,
"direct": 40.35,
"surplus": 6.24032258064517,
"battery": 5.928306451612912,
"imports": 1067.0724999999998,
"base": 7094.794000000002,
"newbill": 3049.1444499999993,
"saving": 4045.6495500000024
},
{
"month": "Feb",
"days": 28,
"G": 50.85535714285714,
"direct": 40.35,
"surplus": 10.505357142857136,
"battery": 9.980089285714278,
"imports": 850.3575000000003,
"base": 6412.071999999999,
"newbill": 2320.490275000001,
"saving": 4091.581724999998
},
{
"month": "Mar",
"days": 31,
"G": 57.15032258064516,
"direct": 40.35,
"surplus": 16.800322580645158,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Apr",
"days": 30,
"G": 58.982,
"direct": 40.35,
"surplus": 18.631999999999998,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "May",
"days": 31,
"G": 57.73935483870968,
"direct": 40.35,
"surplus": 17.38935483870968,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Jun",
"days": 30,
"G": 58.16066666666667,
"direct": 40.35,
"surplus": 17.81066666666667,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Jul",
"days": 31,
"G": 58.42774193548387,
"direct": 40.35,
"surplus": 18.07774193548387,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Aug",
"days": 31,
"G": 59.18709677419355,
"direct": 40.35,
"surplus": 18.837096774193547,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Sep",
"days": 30,
"G": 59.03333333333333,
"direct": 40.35,
"surplus": 18.68333333333333,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Oct",
"days": 31,
"G": 54.833225806451615,
"direct": 40.35,
"surplus": 14.483225806451614,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Nov",
"days": 30,
"G": 50.22233333333334,
"direct": 40.35,
"surplus": 9.872333333333337,
"battery": 9.37871666666667,
"imports": 929.1385,
"base": 6867.22,
"newbill": 2538.7136450000003,
"saving": 4328.5063549999995
},
{
"month": "Dec",
"days": 31,
"G": 46.27096774193549,
"direct": 40.35,
"surplus": 5.920967741935492,
"battery": 5.624919354838717,
"imports": 1076.4774999999997,
"base": 7094.794000000002,
"newbill": 3075.666549999999,
"saving": 4019.1274500000027
}
],
"annualSaving": 53709.35158,
"averageSaving": 4475.779298333334,
"payback": 7.340248735134701,
"annualImports": 10829.596
}

## Slide 15
OPTION B · SOLAR + ONE LV_16
5. Purchase payback and subscription
Simple payback = price / annual saving
= 394,240 / 53,709.35 = 7.34 years
Monthly fee = price / (term in years × 12)
Average net benefit/month = annual saving / 12 − monthly fee
Term | Fee calculation | Fee EGP/month | Avg. net EGP/month
5 years | 394,240 / (5 × 12) | 6,570.67 | -2,094.89
8 years | 394,240 / (8 × 12) | 4,106.67 | 369.11
10 years | 394,240 / (10 × 12) | 3,285.33 | 1,190.45
Break-even term = price / annual saving = 7.34 years, where the average net benefit is zero.
Illustrative recovery of selling price. No extra subscription margin, maintenance, insurance, financing or replacement.
No degradation or tariff increases. Monthly benefits vary. Simple payback is not a discounted return calculation.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
{
"option": "B",
"C": 16,
"P": 11,
"inv": 12,
"price": 394240,
"reference": {
"G": 54.78,
"direct": 40.35,
"surplus": 14.43,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 46.59032258064517,
"direct": 40.35,
"surplus": 6.24032258064517,
"battery": 5.928306451612912,
"imports": 1067.0724999999998,
"base": 7094.794000000002,
"newbill": 3049.1444499999993,
"saving": 4045.6495500000024
},
{
"month": "Feb",
"days": 28,
"G": 50.85535714285714,
"direct": 40.35,
"surplus": 10.505357142857136,
"battery": 9.980089285714278,
"imports": 850.3575000000003,
"base": 6412.071999999999,
"newbill": 2320.490275000001,
"saving": 4091.581724999998
},
{
"month": "Mar",
"days": 31,
"G": 57.15032258064516,
"direct": 40.35,
"surplus": 16.800322580645158,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Apr",
"days": 30,
"G": 58.982,
"direct": 40.35,
"surplus": 18.631999999999998,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "May",
"days": 31,
"G": 57.73935483870968,
"direct": 40.35,
"surplus": 17.38935483870968,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Jun",
"days": 30,
"G": 58.16066666666667,
"direct": 40.35,
"surplus": 17.81066666666667,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Jul",
"days": 31,
"G": 58.42774193548387,
"direct": 40.35,
"surplus": 18.07774193548387,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Aug",
"days": 31,
"G": 59.18709677419355,
"direct": 40.35,
"surplus": 18.837096774193547,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Sep",
"days": 30,
"G": 59.03333333333333,
"direct": 40.35,
"surplus": 18.68333333333333,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Oct",
"days": 31,
"G": 54.833225806451615,
"direct": 40.35,
"surplus": 14.483225806451614,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Nov",
"days": 30,
"G": 50.22233333333334,
"direct": 40.35,
"surplus": 9.872333333333337,
"battery": 9.37871666666667,
"imports": 929.1385,
"base": 6867.22,
"newbill": 2538.7136450000003,
"saving": 4328.5063549999995
},
{
"month": "Dec",
"days": 31,
"G": 46.27096774193549,
"direct": 40.35,
"surplus": 5.920967741935492,
"battery": 5.624919354838717,
"imports": 1076.4774999999997,
"base": 7094.794000000002,
"newbill": 3075.666549999999,
"saving": 4019.1274500000027
}
],
"annualSaving": 53709.35158,
"averageSaving": 4475.779298333334,
"payback": 7.340248735134701,
"annualImports": 10829.596
}

## Slide 16
OPTION C · SOLAR + TWO LV_32
1. Daily demand and system sizing
Daily demand and its split
E = 2,421 / 30 = 80.70 kWh/day; D = N = E × 50% = 40.35
Battery capacity and energy delivered
C = 64 kWh; U = C × 80% = 51.20; U × 95% = 48.64 kWh
PV capacity, rounded up to the next 0.5 kWp
P = (D + min(N, U × η) / η) / Y
= (40.35 + 40.35 / 0.95) / 4.98 = 16.631 → 17.0 kWp
Provisional inverter and roof allowance
Selected inverter I = 20 kW (standard size ≥ P); roof ≈ 17.0 × 6 = 102 m²
Whole-night capacity = N / (DoD × η) = 40.35 / 0.76 = 53.09 kWh. Selected product stack = 64 kWh.
Solar availability still limits nightly delivery. Inverter rating needs motor-surge confirmation.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
{
"option": "C",
"C": 64,
"P": 17,
"inv": 20,
"price": 1154560,
"reference": {
"G": 84.66000000000001,
"direct": 40.35,
"surplus": 44.31000000000001,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 72.00322580645162,
"direct": 40.35,
"surplus": 31.653225806451623,
"battery": 30.07056451612904,
"imports": 318.66249999999985,
"base": 7094.794000000002,
"newbill": 870.8288749999997,
"saving": 6223.965125000002
},
{
"month": "Feb",
"days": 28,
"G": 78.59464285714284,
"direct": 40.35,
"surplus": 38.24464285714284,
"battery": 36.3324107142857,
"imports": 112.49250000000043,
"base": 6412.071999999999,
"newbill": 261.35857500000094,
"saving": 6150.713424999998
},
{
"month": "Mar",
"days": 31,
"G": 88.3232258064516,
"direct": 40.35,
"surplus": 47.9732258064516,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Apr",
"days": 30,
"G": 91.154,
"direct": 40.35,
"surplus": 50.803999999999995,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "May",
"days": 31,
"G": 89.23354838709677,
"direct": 40.35,
"surplus": 48.88354838709677,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Jun",
"days": 30,
"G": 89.88466666666667,
"direct": 40.35,
"surplus": 49.53466666666667,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Jul",
"days": 31,
"G": 90.29741935483871,
"direct": 40.35,
"surplus": 49.94741935483871,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Aug",
"days": 31,
"G": 91.47096774193548,
"direct": 40.35,
"surplus": 51.12096774193548,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Sep",
"days": 30,
"G": 91.23333333333332,
"direct": 40.35,
"surplus": 50.88333333333332,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Oct",
"days": 31,
"G": 84.74225806451614,
"direct": 40.35,
"surplus": 44.392258064516135,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Nov",
"days": 30,
"G": 77.61633333333334,
"direct": 40.35,
"surplus": 37.26633333333334,
"battery": 35.40301666666667,
"imports": 148.40949999999987,
"base": 6867.22,
"newbill": 340.01680499999975,
"saving": 6527.203195
},
{
"month": "Dec",
"days": 31,
"G": 71.50967741935484,
"direct": 40.35,
"surplus": 31.159677419354843,
"battery": 29.6016935483871,
"imports": 333.19749999999993,
"base": 7094.794000000002,
"newbill": 909.6373249999998,
"saving": 6185.156675000002
}
],
"annualSaving": 81090.66842000002,
"averageSaving": 6757.555701666668,
"payback": 14.237889790476089,
"annualImports": 912.7620000000002
}

## Slide 17
OPTION C · SOLAR + TWO LV_32
2. System price
Unit-price assumptions
PV = 8,000 EGP/kWp; inverter = 6,000 EGP/kW
Battery = 220 EUR/kWh × 62 EGP/EUR = 13,640 EGP/kWh
PV and inverter subtotal
17.0 × 8,000 + 20 × 6,000 = 256,000 EGP
Installation / BOS and battery cost
Installation = 256,000 × 10% = 25,600 EGP
Battery = 64 × 13,640 = 872,960 EGP
Total customer price
Price = (17.0 × 8,000 + 20 × 6,000) × 1.10 + 64 × 13,640
= 1,154,560 EGP
The 10% installation/BOS applies to PV and inverter only. Battery price comes from Home_Storage, slide 15.
Customer selling-price assumptions, including historical exchange rate 62 EGP/EUR. These are not current quotes.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
{
"option": "C",
"C": 64,
"P": 17,
"inv": 20,
"price": 1154560,
"reference": {
"G": 84.66000000000001,
"direct": 40.35,
"surplus": 44.31000000000001,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 72.00322580645162,
"direct": 40.35,
"surplus": 31.653225806451623,
"battery": 30.07056451612904,
"imports": 318.66249999999985,
"base": 7094.794000000002,
"newbill": 870.8288749999997,
"saving": 6223.965125000002
},
{
"month": "Feb",
"days": 28,
"G": 78.59464285714284,
"direct": 40.35,
"surplus": 38.24464285714284,
"battery": 36.3324107142857,
"imports": 112.49250000000043,
"base": 6412.071999999999,
"newbill": 261.35857500000094,
"saving": 6150.713424999998
},
{
"month": "Mar",
"days": 31,
"G": 88.3232258064516,
"direct": 40.35,
"surplus": 47.9732258064516,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Apr",
"days": 30,
"G": 91.154,
"direct": 40.35,
"surplus": 50.803999999999995,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "May",
"days": 31,
"G": 89.23354838709677,
"direct": 40.35,
"surplus": 48.88354838709677,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Jun",
"days": 30,
"G": 89.88466666666667,
"direct": 40.35,
"surplus": 49.53466666666667,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Jul",
"days": 31,
"G": 90.29741935483871,
"direct": 40.35,
"surplus": 49.94741935483871,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Aug",
"days": 31,
"G": 91.47096774193548,
"direct": 40.35,
"surplus": 51.12096774193548,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Sep",
"days": 30,
"G": 91.23333333333332,
"direct": 40.35,
"surplus": 50.88333333333332,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Oct",
"days": 31,
"G": 84.74225806451614,
"direct": 40.35,
"surplus": 44.392258064516135,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Nov",
"days": 30,
"G": 77.61633333333334,
"direct": 40.35,
"surplus": 37.26633333333334,
"battery": 35.40301666666667,
"imports": 148.40949999999987,
"base": 6867.22,
"newbill": 340.01680499999975,
"saving": 6527.203195
},
{
"month": "Dec",
"days": 31,
"G": 71.50967741935484,
"direct": 40.35,
"surplus": 31.159677419354843,
"battery": 29.6016935483871,
"imports": 333.19749999999993,
"base": 7094.794000000002,
"newbill": 909.6373249999998,
"saving": 6185.156675000002
}
],
"annualSaving": 81090.66842000002,
"averageSaving": 6757.555701666668,
"payback": 14.237889790476089,
"annualImports": 912.7620000000002
}

## Slide 18
OPTION C · SOLAR + TWO LV_32
3. Energy balance and the monthly bill
Solar generation and direct use
G = P × Y = 17.0 × 4.98 = 84.66 kWh/day
Direct = min(G, D) = 40.35; surplus = G − Direct = 44.31
Battery energy delivered to the loads
B = min(surplus × η, U × η, N)
= min(42.09, 48.64, 40.35) = 40.35 kWh/day
Grid imports in the 30-day reference month
M_grid = (E − Direct − B) × 30
= (80.70 − 40.35 − 40.35) × 30 = 0.00 kWh
New bill and monthly saving
Bill = zero-use service fee = 9.00 EGP
Saving = 6,867.22 − 9.00 = 6,858.22 EGP
This is a 30-day example at Y = 4.98. Solar charges the battery. Surplus export earns zero revenue.
Storage losses are applied once. The annual calculation on the next slide accounts for monthly solar variation.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
{
"option": "C",
"C": 64,
"P": 17,
"inv": 20,
"price": 1154560,
"reference": {
"G": 84.66000000000001,
"direct": 40.35,
"surplus": 44.31000000000001,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 72.00322580645162,
"direct": 40.35,
"surplus": 31.653225806451623,
"battery": 30.07056451612904,
"imports": 318.66249999999985,
"base": 7094.794000000002,
"newbill": 870.8288749999997,
"saving": 6223.965125000002
},
{
"month": "Feb",
"days": 28,
"G": 78.59464285714284,
"direct": 40.35,
"surplus": 38.24464285714284,
"battery": 36.3324107142857,
"imports": 112.49250000000043,
"base": 6412.071999999999,
"newbill": 261.35857500000094,
"saving": 6150.713424999998
},
{
"month": "Mar",
"days": 31,
"G": 88.3232258064516,
"direct": 40.35,
"surplus": 47.9732258064516,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Apr",
"days": 30,
"G": 91.154,
"direct": 40.35,
"surplus": 50.803999999999995,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "May",
"days": 31,
"G": 89.23354838709677,
"direct": 40.35,
"surplus": 48.88354838709677,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Jun",
"days": 30,
"G": 89.88466666666667,
"direct": 40.35,
"surplus": 49.53466666666667,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Jul",
"days": 31,
"G": 90.29741935483871,
"direct": 40.35,
"surplus": 49.94741935483871,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Aug",
"days": 31,
"G": 91.47096774193548,
"direct": 40.35,
"surplus": 51.12096774193548,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Sep",
"days": 30,
"G": 91.23333333333332,
"direct": 40.35,
"surplus": 50.88333333333332,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Oct",
"days": 31,
"G": 84.74225806451614,
"direct": 40.35,
"surplus": 44.392258064516135,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Nov",
"days": 30,
"G": 77.61633333333334,
"direct": 40.35,
"surplus": 37.26633333333334,
"battery": 35.40301666666667,
"imports": 148.40949999999987,
"base": 6867.22,
"newbill": 340.01680499999975,
"saving": 6527.203195
},
{
"month": "Dec",
"days": 31,
"G": 71.50967741935484,
"direct": 40.35,
"surplus": 31.159677419354843,
"battery": 29.6016935483871,
"imports": 333.19749999999993,
"base": 7094.794000000002,
"newbill": 909.6373249999998,
"saving": 6185.156675000002
}
],
"annualSaving": 81090.66842000002,
"averageSaving": 6757.555701666668,
"payback": 14.237889790476089,
"annualImports": 912.7620000000002
}

## Slide 19
OPTION C · SOLAR + TWO LV_32
4. Twelve monthly results and annual saving
Each month: daily PV = P × PVGIS monthly kWh/kWp ÷ days. Grid = (E − Direct − B) × days.
Month | Days | PV kWh | Grid kWh | Baseline EGP | New bill EGP | Saving EGP
Jan | 31 | 2,232.10 | 318.66 | 7,094.79 | 870.83 | 6,223.97
Feb | 28 | 2,200.65 | 112.49 | 6,412.07 | 261.36 | 6,150.71
Mar | 31 | 2,738.02 | 0.00 | 7,094.79 | 9.00 | 7,085.79
Apr | 30 | 2,734.62 | 0.00 | 6,867.22 | 9.00 | 6,858.22
May | 31 | 2,766.24 | 0.00 | 7,094.79 | 9.00 | 7,085.79
Jun | 30 | 2,696.54 | 0.00 | 6,867.22 | 9.00 | 6,858.22
Jul | 31 | 2,799.22 | 0.00 | 7,094.79 | 9.00 | 7,085.79
Aug | 31 | 2,835.60 | 0.00 | 7,094.79 | 9.00 | 7,085.79
Sep | 30 | 2,737.00 | 0.00 | 6,867.22 | 9.00 | 6,858.22
Oct | 31 | 2,627.01 | 0.00 | 7,094.79 | 9.00 | 7,085.79
Nov | 30 | 2,328.49 | 148.41 | 6,867.22 | 340.02 | 6,527.20
Dec | 31 | 2,216.80 | 333.20 | 7,094.79 | 909.64 | 6,185.16
Year | 365 | 30,912.29 | 912.76 | 83,544.51 | 2,453.84 | 81,090.67
Annual saving = sum of monthly savings = 81,090.67 EGP. Average/month = annual / 12 = 6,757.56 EGP.
Constant demand: 80.7 kWh/day, 50/50 split. Monthly average days, no hourly simulation. Displayed figures are rounded.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
{
"option": "C",
"C": 64,
"P": 17,
"inv": 20,
"price": 1154560,
"reference": {
"G": 84.66000000000001,
"direct": 40.35,
"surplus": 44.31000000000001,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 72.00322580645162,
"direct": 40.35,
"surplus": 31.653225806451623,
"battery": 30.07056451612904,
"imports": 318.66249999999985,
"base": 7094.794000000002,
"newbill": 870.8288749999997,
"saving": 6223.965125000002
},
{
"month": "Feb",
"days": 28,
"G": 78.59464285714284,
"direct": 40.35,
"surplus": 38.24464285714284,
"battery": 36.3324107142857,
"imports": 112.49250000000043,
"base": 6412.071999999999,
"newbill": 261.35857500000094,
"saving": 6150.713424999998
},
{
"month": "Mar",
"days": 31,
"G": 88.3232258064516,
"direct": 40.35,
"surplus": 47.9732258064516,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Apr",
"days": 30,
"G": 91.154,
"direct": 40.35,
"surplus": 50.803999999999995,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "May",
"days": 31,
"G": 89.23354838709677,
"direct": 40.35,
"surplus": 48.88354838709677,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Jun",
"days": 30,
"G": 89.88466666666667,
"direct": 40.35,
"surplus": 49.53466666666667,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Jul",
"days": 31,
"G": 90.29741935483871,
"direct": 40.35,
"surplus": 49.94741935483871,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Aug",
"days": 31,
"G": 91.47096774193548,
"direct": 40.35,
"surplus": 51.12096774193548,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Sep",
"days": 30,
"G": 91.23333333333332,
"direct": 40.35,
"surplus": 50.88333333333332,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Oct",
"days": 31,
"G": 84.74225806451614,
"direct": 40.35,
"surplus": 44.392258064516135,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Nov",
"days": 30,
"G": 77.61633333333334,
"direct": 40.35,
"surplus": 37.26633333333334,
"battery": 35.40301666666667,
"imports": 148.40949999999987,
"base": 6867.22,
"newbill": 340.01680499999975,
"saving": 6527.203195
},
{
"month": "Dec",
"days": 31,
"G": 71.50967741935484,
"direct": 40.35,
"surplus": 31.159677419354843,
"battery": 29.6016935483871,
"imports": 333.19749999999993,
"base": 7094.794000000002,
"newbill": 909.6373249999998,
"saving": 6185.156675000002
}
],
"annualSaving": 81090.66842000002,
"averageSaving": 6757.555701666668,
"payback": 14.237889790476089,
"annualImports": 912.7620000000002
}

## Slide 20
OPTION C · SOLAR + TWO LV_32
5. Purchase payback and subscription
Simple payback = price / annual saving
= 1,154,560 / 81,090.67 = 14.24 years
Monthly fee = price / (term in years × 12)
Average net benefit/month = annual saving / 12 − monthly fee
Term | Fee calculation | Fee EGP/month | Avg. net EGP/month
5 years | 1,154,560 / (5 × 12) | 19,242.67 | -12,485.11
8 years | 1,154,560 / (8 × 12) | 12,026.67 | -5,269.11
10 years | 1,154,560 / (10 × 12) | 9,621.33 | -2,863.78
Break-even term = price / annual saving = 14.24 years, where the average net benefit is zero.
Illustrative recovery of selling price. No extra subscription margin, maintenance, insurance, financing or replacement.
No degradation or tariff increases. Monthly benefits vary. Simple payback is not a discounted return calculation.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
{
"option": "C",
"C": 64,
"P": 17,
"inv": 20,
"price": 1154560,
"reference": {
"G": 84.66000000000001,
"direct": 40.35,
"surplus": 44.31000000000001,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 72.00322580645162,
"direct": 40.35,
"surplus": 31.653225806451623,
"battery": 30.07056451612904,
"imports": 318.66249999999985,
"base": 7094.794000000002,
"newbill": 870.8288749999997,
"saving": 6223.965125000002
},
{
"month": "Feb",
"days": 28,
"G": 78.59464285714284,
"direct": 40.35,
"surplus": 38.24464285714284,
"battery": 36.3324107142857,
"imports": 112.49250000000043,
"base": 6412.071999999999,
"newbill": 261.35857500000094,
"saving": 6150.713424999998
},
{
"month": "Mar",
"days": 31,
"G": 88.3232258064516,
"direct": 40.35,
"surplus": 47.9732258064516,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Apr",
"days": 30,
"G": 91.154,
"direct": 40.35,
"surplus": 50.803999999999995,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "May",
"days": 31,
"G": 89.23354838709677,
"direct": 40.35,
"surplus": 48.88354838709677,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Jun",
"days": 30,
"G": 89.88466666666667,
"direct": 40.35,
"surplus": 49.53466666666667,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Jul",
"days": 31,
"G": 90.29741935483871,
"direct": 40.35,
"surplus": 49.94741935483871,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Aug",
"days": 31,
"G": 91.47096774193548,
"direct": 40.35,
"surplus": 51.12096774193548,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Sep",
"days": 30,
"G": 91.23333333333332,
"direct": 40.35,
"surplus": 50.88333333333332,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Oct",
"days": 31,
"G": 84.74225806451614,
"direct": 40.35,
"surplus": 44.392258064516135,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Nov",
"days": 30,
"G": 77.61633333333334,
"direct": 40.35,
"surplus": 37.26633333333334,
"battery": 35.40301666666667,
"imports": 148.40949999999987,
"base": 6867.22,
"newbill": 340.01680499999975,
"saving": 6527.203195
},
{
"month": "Dec",
"days": 31,
"G": 71.50967741935484,
"direct": 40.35,
"surplus": 31.159677419354843,
"battery": 29.6016935483871,
"imports": 333.19749999999993,
"base": 7094.794000000002,
"newbill": 909.6373249999998,
"saving": 6185.156675000002
}
],
"annualSaving": 81090.66842000002,
"averageSaving": 6757.555701666668,
"payback": 14.237889790476089,
"annualImports": 912.7620000000002
}

## Slide 21
FINAL COMPARISON
A, B and C: equations and final results
Metric / equation | A · Solar only | B · Solar + 16 kWh | C · Solar + 64 kWh
PV P / battery C / inverter | 8.5 kWp / 0 kWh / 10 kW | 11.0 kWp / 16 kWh / 12 kW | 17.0 kWp / 64 kWh / 20 kW
Price = (8,000P + 6,000I) × 1.1 + 13,640C | 140,800 EGP | 394,240 EGP | 1,154,560 EGP
Delivered battery = min(surplus × η, U × η, N) | 0.00 kWh/day | 12.16 kWh/day | 40.35 kWh/day
30-day grid = (E − Direct − B) × 30 | 1,210.50 kWh | 845.70 kWh | 0.00 kWh
30-day saving = 6,867.22 − new bill | 3,413.61 EGP | 4,559.63 EGP | 6,858.22 EGP
Annual saving = sum of 12 monthly savings | 40,537 EGP | 53,709 EGP | 81,091 EGP
Average monthly saving = annual / 12 | 3,378 EGP | 4,476 EGP | 6,758 EGP
Simple payback = price / annual saving | 3.47 years | 7.34 years | 14.24 years
10-year fee = price / 120 | 1,173 EGP/month | 3,285 EGP/month | 9,621 EGP/month
Avg. net/month = annual / 12 − 10-year fee | 2,205 EGP/month | 1,190 EGP/month | -2,864 EGP/month
Roof allowance = P × 6 | 51 m² | 66 m² | 102 m²
All three use the same 50/50 demand split, prices and tariff. The 30-day example and annual averages have different bases.
Annual results assume constant daily demand and monthly PVGIS output. Larger storage does not guarantee zero winter imports.
Notes: Same assumptions and calculation basis as El_Mo3alem_Juice_Shop_Solar_BESS.pptx, reviewed 30 Sep 2026. Baseline80.7 kWh/day,50/50,PV mean4.98,DoD80%,storage efficiency95% applied once at output. Prices are historical selling-price assumptions. Battery220 EUR/kWh*62EGP/EUR=13640EGP/kWh from Home_Storage slide15. Tariff source https://www.egyptera.org/en/TarrifApril2026.aspx . PV source JRC PVGIS5.3: https://re.jrc.ec.europa.eu/api/v5_3/PVcalc?lat=30.0444&lon=31.2357&peakpower=1&loss=14&angle=30&aspect=0&pvtechchoice=crystSi&mountingplace=free&outputformat=json . SARAH3/ERA5 2005–2023. 30degree south-facing free-standing crystalline silicon,14% entered PV loss. Solar-only charging, zero export value. No maintenance, insurance, finance, replacement, degradation or price escalation. Annual3EGP stamp excluded equally. Monthly-average days rather than hourly dispatch, daily demand constant over365days. Unrounded values used, display rounding may differ. Billing-period30days assumed. Inverter and roof sizing provisional. Warranty10years,6000cycles@80%DoD from original source.
[
{
"option": "A",
"C": 0,
"P": 8.5,
"inv": 10,
"price": 140800,
"reference": {
"G": 42.330000000000005,
"direct": 40.35,
"surplus": 1.980000000000004,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 36.00161290322581,
"direct": 36.00161290322581,
"surplus": 0,
"battery": 0,
"imports": 1385.6499999999999,
"base": 7094.794000000002,
"newbill": 3947.533,
"saving": 3147.261000000002
},
{
"month": "Feb",
"days": 28,
"G": 39.29732142857142,
"direct": 39.29732142857142,
"surplus": 0,
"battery": 0,
"imports": 1159.2750000000003,
"base": 6412.071999999999,
"newbill": 3309.1555000000008,
"saving": 3102.9164999999985
},
{
"month": "Mar",
"days": 31,
"G": 44.1616129032258,
"direct": 40.35,
"surplus": 3.8116129032258,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Apr",
"days": 30,
"G": 45.577,
"direct": 40.35,
"surplus": 5.226999999999997,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "May",
"days": 31,
"G": 44.61677419354839,
"direct": 40.35,
"surplus": 4.266774193548386,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Jun",
"days": 30,
"G": 44.94233333333334,
"direct": 40.35,
"surplus": 4.592333333333336,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Jul",
"days": 31,
"G": 45.148709677419355,
"direct": 40.35,
"surplus": 4.798709677419353,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Aug",
"days": 31,
"G": 45.73548387096774,
"direct": 40.35,
"surplus": 5.3854838709677395,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Sep",
"days": 30,
"G": 45.61666666666666,
"direct": 40.35,
"surplus": 5.266666666666659,
"battery": 0,
"imports": 1210.5,
"base": 6867.22,
"newbill": 3453.61,
"saving": 3413.61
},
{
"month": "Oct",
"days": 31,
"G": 42.37112903225807,
"direct": 40.35,
"surplus": 2.0211290322580666,
"battery": 0,
"imports": 1250.8500000000001,
"base": 7094.794000000002,
"newbill": 3567.397000000001,
"saving": 3527.397000000001
},
{
"month": "Nov",
"days": 30,
"G": 38.80816666666667,
"direct": 38.80816666666667,
"surplus": 0,
"battery": 0,
"imports": 1256.7549999999999,
"base": 6867.22,
"newbill": 3584.0490999999997,
"saving": 3283.1709000000005
},
{
"month": "Dec",
"days": 31,
"G": 35.75483870967742,
"direct": 35.75483870967742,
"surplus": 0,
"battery": 0,
"imports": 1393.3,
"base": 7094.794000000002,
"newbill": 3969.1059999999998,
"saving": 3125.688000000002
}
],
"annualSaving": 40536.85140000001,
"averageSaving": 3378.0709500000007,
"payback": 3.4733827403279767,
"annualImports": 15080.73
},
{
"option": "B",
"C": 16,
"P": 11,
"inv": 12,
"price": 394240,
"reference": {
"G": 54.78,
"direct": 40.35,
"surplus": 14.43,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 46.59032258064517,
"direct": 40.35,
"surplus": 6.24032258064517,
"battery": 5.928306451612912,
"imports": 1067.0724999999998,
"base": 7094.794000000002,
"newbill": 3049.1444499999993,
"saving": 4045.6495500000024
},
{
"month": "Feb",
"days": 28,
"G": 50.85535714285714,
"direct": 40.35,
"surplus": 10.505357142857136,
"battery": 9.980089285714278,
"imports": 850.3575000000003,
"base": 6412.071999999999,
"newbill": 2320.490275000001,
"saving": 4091.581724999998
},
{
"month": "Mar",
"days": 31,
"G": 57.15032258064516,
"direct": 40.35,
"surplus": 16.800322580645158,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Apr",
"days": 30,
"G": 58.982,
"direct": 40.35,
"surplus": 18.631999999999998,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "May",
"days": 31,
"G": 57.73935483870968,
"direct": 40.35,
"surplus": 17.38935483870968,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Jun",
"days": 30,
"G": 58.16066666666667,
"direct": 40.35,
"surplus": 17.81066666666667,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Jul",
"days": 31,
"G": 58.42774193548387,
"direct": 40.35,
"surplus": 18.07774193548387,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Aug",
"days": 31,
"G": 59.18709677419355,
"direct": 40.35,
"surplus": 18.837096774193547,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Sep",
"days": 30,
"G": 59.03333333333333,
"direct": 40.35,
"surplus": 18.68333333333333,
"battery": 12.16,
"imports": 845.7,
"base": 6867.22,
"newbill": 2307.5890000000004,
"saving": 4559.630999999999
},
{
"month": "Oct",
"days": 31,
"G": 54.833225806451615,
"direct": 40.35,
"surplus": 14.483225806451614,
"battery": 12.16,
"imports": 873.89,
"base": 7094.794000000002,
"newbill": 2385.6753,
"saving": 4709.118700000002
},
{
"month": "Nov",
"days": 30,
"G": 50.22233333333334,
"direct": 40.35,
"surplus": 9.872333333333337,
"battery": 9.37871666666667,
"imports": 929.1385,
"base": 6867.22,
"newbill": 2538.7136450000003,
"saving": 4328.5063549999995
},
{
"month": "Dec",
"days": 31,
"G": 46.27096774193549,
"direct": 40.35,
"surplus": 5.920967741935492,
"battery": 5.624919354838717,
"imports": 1076.4774999999997,
"base": 7094.794000000002,
"newbill": 3075.666549999999,
"saving": 4019.1274500000027
}
],
"annualSaving": 53709.35158,
"averageSaving": 4475.779298333334,
"payback": 7.340248735134701,
"annualImports": 10829.596
},
{
"option": "C",
"C": 64,
"P": 17,
"inv": 20,
"price": 1154560,
"reference": {
"G": 84.66000000000001,
"direct": 40.35,
"surplus": 44.31000000000001,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
"monthly": [
{
"month": "Jan",
"days": 31,
"G": 72.00322580645162,
"direct": 40.35,
"surplus": 31.653225806451623,
"battery": 30.07056451612904,
"imports": 318.66249999999985,
"base": 7094.794000000002,
"newbill": 870.8288749999997,
"saving": 6223.965125000002
},
{
"month": "Feb",
"days": 28,
"G": 78.59464285714284,
"direct": 40.35,
"surplus": 38.24464285714284,
"battery": 36.3324107142857,
"imports": 112.49250000000043,
"base": 6412.071999999999,
"newbill": 261.35857500000094,
"saving": 6150.713424999998
},
{
"month": "Mar",
"days": 31,
"G": 88.3232258064516,
"direct": 40.35,
"surplus": 47.9732258064516,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Apr",
"days": 30,
"G": 91.154,
"direct": 40.35,
"surplus": 50.803999999999995,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "May",
"days": 31,
"G": 89.23354838709677,
"direct": 40.35,
"surplus": 48.88354838709677,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Jun",
"days": 30,
"G": 89.88466666666667,
"direct": 40.35,
"surplus": 49.53466666666667,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Jul",
"days": 31,
"G": 90.29741935483871,
"direct": 40.35,
"surplus": 49.94741935483871,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Aug",
"days": 31,
"G": 91.47096774193548,
"direct": 40.35,
"surplus": 51.12096774193548,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Sep",
"days": 30,
"G": 91.23333333333332,
"direct": 40.35,
"surplus": 50.88333333333332,
"battery": 40.35,
"imports": 0,
"base": 6867.22,
"newbill": 9,
"saving": 6858.22
},
{
"month": "Oct",
"days": 31,
"G": 84.74225806451614,
"direct": 40.35,
"surplus": 44.392258064516135,
"battery": 40.35,
"imports": 0,
"base": 7094.794000000002,
"newbill": 9,
"saving": 7085.794000000002
},
{
"month": "Nov",
"days": 30,
"G": 77.61633333333334,
"direct": 40.35,
"surplus": 37.26633333333334,
"battery": 35.40301666666667,
"imports": 148.40949999999987,
"base": 6867.22,
"newbill": 340.01680499999975,
"saving": 6527.203195
},
{
"month": "Dec",
"days": 31,
"G": 71.50967741935484,
"direct": 40.35,
"surplus": 31.159677419354843,
"battery": 29.6016935483871,
"imports": 333.19749999999993,
"base": 7094.794000000002,
"newbill": 909.6373249999998,
"saving": 6185.156675000002
}
],
"annualSaving": 81090.66842000002,
"averageSaving": 6757.555701666668,
"payback": 14.237889790476089,
"annualImports": 912.7620000000002
}
]