AVESTA Egypt

# Juice Shop Electricity and BESS Assessment

Engineering and Management  |  25 September 2026  |  Internal circulation

# Executive assessment

The receipt records 2,421 kWh and EGP 8,279 paid. The equipment estimates totals 66.1 kWh/day, below the receipt-based 80.7 kWh/day planning baseline. Investigate this gap before final battery energy storage system (BESS) sizing. The 15–20 kW inverter and 80–120 kWh usable battery range remains preliminary, pending measurement and an agreed backup objective.

# Verified receipt figures

| Receipt item | Verified value |
| --- | --- |
| Billing reference and payment | August 2026 ¦ EGP 8,279 |
| Current and previous readings | 312,070 kWh ¦ 309,649 kWh |
| Monthly consumption | 2,421 kWh |

Meter check: 312,070 − 309,649 = 2,421 kWh. Average daily energy is approximately 80.7 kWh/day using a 30-day planning basis. August has 31 calendar days, which would give 78.1 kWh/day; confirm the actual meter-reading interval before final modelling.

# Estimated equipment demand

| Equipment | Qty | Power per unit | Daily operation | kWh/day |
| --- | --- | --- | --- | --- |
| Coca-Cola single-door refrigerator | 3 | 439 W | 24 h with cycling | 14.2 |
| Coca-Cola double-door refrigerator | 2 | 645 W | 24 h with cycling | 13.9 |
| Ice-cream freezer | 3 | 330 W | 24 h with cycling | 14.3 |
| 3-phase 3-roll sugarcane juicer | 1 | 2.2 kW | 6 equivalent full-load h | 13.2 |
| LED lights | 25 | 12 W | 15 h | 4.5 |
| Commercial blender | 1 | 1.5 kW | 2 equivalent full-load h | 3.0 |
| Carrot juicer | 1 | 0.75 kW | 2 equivalent full-load h | 1.5 |
| Ice crusher / ice shaver | 1 | 0.5 kW | 3 equivalent full-load h | 1.5 |
| Total |  | 8.85 kW connected |  | 66.1 |

All equipment powers and operating patterns are estimates, not measured ratings. Refrigeration energy implies approximately 45% of compressor duty for the refrigerators and 60% for the freezers. Confirm whether the juicer rating is electrical input or motor shaft output.

Reconciliation: 66.1 × 30 = 1,983 kWh/month, leaving 438 kWh/month (14.6 kWh/day), or 18.1% of receipt of consumption, unexplained by the estimate. Higher compressor duty, longer use, omitted loads or rating differences are possible explanations, not established findings. Use measured total energy as the baseline while investigating the gap.

# Engineering interpretation

Monthly kWh is energy, not peak kW. Using 80.7 kWh/day, equivalent average operating loads are 6.7 kW at 12 hours/day, 5.8 kW at 14 hours, 5.0 kW at 16 hours, and 4.5 kW at 18 hours. These allocate all daily energy to opening hours; refrigeration runs overnight, so they are not measuring opening-hour averages. The estimated 8.85 kW connected load is neither measured peak demand nor motor-start surge.

# Preliminary BESS sizing

| Parameter | Preliminary engineering review range |
| --- | --- |
| Inverter continuous output | Approximately 15–20 kW |
| Battery usable energy | Approximately 80–120 kWh |

These are screening assumptions, not validated specifications. The 15–20 kW inverter range exceeds the estimated 8.85 kW connected load and may be conservative; it is not justified by the receipt alone. Check measured kW/kVA, power factor, phase balance and compressor/motor starting currents and durations. Confirm three-phase backup compatibility for the sugarcane juicer and surge capability at site temperature.

The usable battery range is approximately 1.0–1.5 times planning daily energy. At a constant 5 kW, it represents 16–24 hours before inverter losses, auxiliary consumption and additional reserve, not guaranteed whole-shop autonomy. Specify usable versus nameplate capacity and account for discharge limits, ageing and temperature.

For backup, size energy against the critical-load profile and required outage duration. For peak shaving, size against the energy above the chosen grid-demand limit; a smaller battery may suffice. Confirm recharge capacity and time between events. Backup reserve reduces capacity available for tariff optimization, so the same stored energy cannot be counted twice.

# Management implications

The observed baseline is EGP 8,279 paid for 2,421 kWh. The payment receipt has no detailed charge line items; it cannot confirm the applicable unit tariff, demand charges, time-of-use pricing or any surcharge. Obtain the detailed invoice before attributing charges or forecasting savings.

Evaluate three objectives: peak shaving to reduce grid peaks where operationally or financially valuable; backup to protect refrigeration and continuity of service; and tariff optimization where verified price differences or solar self-consumption create value. A battery does not generate energy, and grid charging adds losses. Bill reduction and payback are therefore unproven at this stage.

Basis: August 2026 payment receipt and reported equipment inventory. Method reference: NREL System Advisor Model, Battery Storage — https://sam.nrel.gov/index.php?Itemid=360&id=94&option=com_content&view=article