# Peak Time Battery Savings

El Mo3alem shop | Evidence, assumptions and calculations | 27 October 2026

# 1  Evidence of possible peak pricing

Historical official evidence: EgyptERA listed separate off-peak and peak prices for certain voltage categories in January-July 2024. For other medium-voltage users, these were EGP 1.282 and 1.923/kWh. This establishes historical time-based pricing, not its application to ordinary commercial shops. [1] Official historical tariff

Press evidence: Masrawy reported on 29 June 2026, citing ministry sources, a 20% premium on peak-period consumption for some commercial customers. This supports investigating the possibility but does not verify the tariff for this shop. [2] Masrawy report

Current official baseline: the published April 2026 table gives EGP 2.79/kWh for commercial consumption above 1,000 kWh/month, without a separate commercial peak-price schedule. No current official peak rate applicable to this shop has been verified; the premium below is therefore an assumption. [3] Official April 2026 tariff

# 2  Calculation assumptions

| Input | Value |
| --- | --- |
| Shop consumption and billing period | 2,421 kWh per 30-day month |
| Energy prices | Base: EGP 2.79/kWh [3]; assumed peak premium: 20% |
| Peak period and operation | 4 hours/day; same daily profile; grid charging outside peak |
| Battery assumptions supplied by the user | 80% usable capacity; 100% charge/discharge/conversion efficiency |
| Available nominal battery sizes | 5, 16 and 32 kWh; usable energy: 4, 12.8 and 25.6 kWh |

Full peak-energy coverage is assumed. No battery losses, additional backup reserve, degradation or ownership costs are deducted. No peak-demand charge saving is included.

# 3  Uniform consumption calculation

Peak price = 2.79 x 1.20 = EGP 3.348/kWh

Price difference = 3.348 - 2.79 = EGP 0.558/kWh

Monthly peak energy = 2,421 x (4 / 24) = 403.5 kWh

Monthly surcharge = monthly battery saving = 403.5 x 0.558 = EGP 225.15

Energy-only bill: EGP 6,754.59 without premium; EGP 6,979.74 with premium

Energy-bill increase = (4 / 24) x 20% = 3.33%

Daily battery output = 403.5 / 30 = 13.45 kWh

Required nominal capacity = 13.45 / 0.80 = 16.8125 kWh

# 4  Higher peak consumption scenarios

Monthly consumption remains 2,421 kWh. These are worse cases for the bill and better opportunities for battery savings. The 50% and 75% shares are hypothetical; 100% is a theoretical upper bound, not a measured shop profile.

For peak share f: monthly peak energy = 2,421 x f

Monthly saving = 2,421 x f x 0.558

Required nominal capacity = (2,421 x f / 30) / 0.80

Average power over the 4-hour peak = (2,421 x f / 30) / 4

| Peak share | Peak energy kWh/month | Saving EGP/month | Daily output kWh | Nominal need kWh |
| --- | --- | --- | --- | --- |
| 16.67% | 403.50 | 225.15 | 13.450 | 16.813 |
| 50% | 1,210.50 | 675.46 | 40.350 | 50.438 |
| 75% | 1,815.75 | 1,013.19 | 60.525 | 75.656 |
| 100% | 2,421.00 | 1,350.92 | 80.700 | 100.875 |

Example at 75%: 1,815.75 / 30 = 60.525 kWh/day; 60.525 / 0.80 = 75.65625 kWh nominal; average peak power = 15.13125 kW. Monthly saving = EGP 1,013.19.

# 5  Battery quantities for full coverage

Unit count = round UP [daily peak energy / (0.80 x nominal unit size)]

| Peak share | 5 kWh units | 16 kWh units | 32 kWh units |
| --- | --- | --- | --- |
| 16.67% | 4 | 2 | 1 |
| 50% | 11 | 4 | 2 |
| 75% | 16 | 5 | 3 |
| 100% | 21 | 7 | 4 |

Each column is a separate same-size option. At 75%, five 16 kWh units provide 80 kWh nominal and 64 kWh usable. Energy capacity alone does not establish suitability: battery/inverter power, charging capability and permitted parallel unit counts must also be verified.

# 6  Observations and conclusion

With 100% efficiency, bill savings equal the avoided premium: EGP 225.15/month for uniform consumption, EGP 1,013.19 at 75%, and a theoretical maximum of EGP 1,350.92 at 100%. Extra battery capacity does not increase savings after all peak energy is covered.

These savings appear unlikely to recover the battery system cost on their own. Peak-time savings should therefore be treated as an additional benefit, not the primary purpose of installing the battery. This is a preliminary observation; a definitive payback conclusion requires installed prices, expected life and replacement costs.

Actual savings depend on confirmation of the shop tariff and measured consumption timing. Backup power and avoided outage losses may provide a separate justification. The 20% premium is not established by the observed EGP 8,279 bill.